## GiM
GRUNDFOS CIM/CIU MODBUS PROFILE FOR GRUNDFOS iSOLUTION MONITOR (GiM)
All addresses are registers (16 bit), and the address is written in decimal format.
Sheet version: V01.13..01
Change date (d-m-y): 30-06-2021
Reg. addr. | Access | Modbus parameter name | Description | Bool/Enum description | Modbus Scale | Modbus Unit
CIM DEVICE CONFIG [R/W] - All saved in EEPROM
00003 | [R/W] | Config.ModbusAddress | Modbus slave address. Valid range [1; 247], default 247. Saved in EEPROM. | unsigned |  | unscaled
00004 | [R/W] | Config.ModbusBitRate | Transmission bit rate, default 9600 bits/s. Saved in EEPROM. | 3 = 9600 4 = 19200 5 = 38400 9 = 115200 |  | enum
00005 | [R/W] | Config.AutoAckControlBits | Acknowlege behaviour of control bits 0 = Controls bits are manually lowered. 1 = Control bits are automatically lowered, default Saved in EEPROM. | 0 = Manual, 1 = Automatic |  | bool
00009 | [R/W] | Config.ModbusParity | Default value = 0. Saved in EEPROM. | 0 = No parity 1 = Even parity 2 = Odd parity |  | enum
00010 | [R/W] | Config.ModbusStopBits | Default value = 1. Saved in EEPROM. | 0 = Not defined 1 = 1 stop bit 2 = 2 stop bit |  | enum
CIM DEVICE STATUS [R]
00030 | [R] | GrundfosUnitFamily | Grundfos product device family | 0 = - 1 = MAGNA series 2 = MGE series 7 = Motor Protection Unit 17 = Multi-E booster 21 = MPC / Multi-B 25 = CR Monitor 26 = Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller CU 2X1 48 = Level controller LC 2x1 56 = GiM (iPump) 255 = N/A |  | enum
00031 | [R] | GrundfosUnitType | Grundfos product device type number |  |  | unscaled
00032 | [R] | GrundfosUnitVersion | Grundfos product device version number |  |  | unscaled
00038 | [R] | FieldbusProtocolVersion | Fieldbus protocol version (BCD digit 1-4 aa.bb), GiM 0.5 only, RESERVED in manual |  |  | BCD number
00039 | [R] | LDUProtocolVersion | LDU protocol version (BCD digit 1-4 aa.bb), GiM 0.5 only, RESERVED in manual |  |  | BCD number
00040 | [R] | GENIbusProtocolVersion | GENIbus protocol version (BCD digit 1-4 aa.bb), GiM 0.5 only, RESERVED in manual |  |  | BCD number
00041 | [R] | GatewayVersion | Gateway version (BCD digit 1-4 aa.bb), GiM 0.5 only, RESERVED in manual |  |  | BCD number
00042 | [R] | LDUSoftwareVersion | LDU software version (BCD digit 1-4 aa.bb), GiM 0.5 only, RESERVED in manual |  |  | BCD number
00043 | [R] | LDUProtocolVersion | LDU protocol version (BCD digit 1-4 aa.bb), GiM 0.5 only, RESERVED in manual |  |  | BCD number
00044 | [R] | GatewaySoftwareDayMonth | Product software date (BCD ddmm), GiM 0.5 only, RESERVED in manual |  |  | BCD number
00045 | [R] | GatewaySoftwareDayYear | Product software date (BCD yyyy), GiM 0.5 only, RESERVED in manual |  |  | BCD number
00046 | [R] | GiMIOBoardSoftwareVersionHI | GiM IO-board software version high (BCD digit 1-4 aa.bb), GiM 1.x only |  |  | BCD number
00047 | [R] | GiMIOBoardSoftwareVersionLO | GiM IO-board software version low (BCD digit 5-8 cc.dd), GiM 1.x only |  |  | BCD number
00048 | [R] | GiMIOBoardSoftwareBuildHI | GiM IO-board software build (BCD digit 1) |  |  | BCD number
00049 | [R] | GiMIOBoardSoftwareBuildLO | GiM IO-board software version (BCD digit 2-5) |  |  | BCD number
00050 | [R] | GiMIOBoardSoftwareDayMonth | GiM IO-board software date (BCD ddmm), GiM 1.x only |  |  | BCD number
00051 | [R] | GiMIOBoardSoftwareDayYear | GiM IO-board software date (BCD yyyy), GiM 1.x only |  |  | BCD number
00052 | [R] | GiMVTUBoardSoftwareVersionHI | GiM VTU-board software version high (BCD digit 1-4 aa.bb), GiM 1.x only |  |  | BCD number
00053 | [R] | GiMVTUBoardSoftwareVersionLO | GiM VTU-board software version low (BCD digit 5-8 cc.dd), GiM 1.x only |  |  | BCD number
00054 | [R] | GiMVTUBoardSoftwareBuildHI | GiM VTU-board software build (BCD digit 1) |  |  | BCD number
00055 | [R] | GiMVTUBoardSoftwareBuildLO | GiM VTU-board software version (BCD digit 2-5) |  |  | BCD number
GiM CONTROL and CONFIGURATION [W]
00101.0 | [W] | Control.ResetAlarm | Resets alarms and warnings | 0 = No resetting 1 = Reset alarm |  | bool
GiM STATUS [R]
00201.0 | [R] | Status.ResetAlarmAck | Acknowledge of ResetAlarm | 0 = No acknowledge 1 = Acknowledged |  | bool
00202 | [R] | Status.WarningCode | Grundfos-specific warning code | 3 = External alarm from DI 24 = Mechanical vibration critical 30 = Change bearings 44 = Undertemperature 46 = External warning (fault 2) from DI 57 = Dry-running state for more than 10s 61 = Water hammer is critical 64 = Overtemperature 76 = Internal communication error 88 = Sensor fault or no sensor attached 131 = Mechanical unbalamce is critical 133 = Generic sensor limit exceeded 152 = Add-on module comm. fault 157 = Real time clock fault 159 = CIM module comm. fault 162 = Sensor supply fault, 24V 165 = Generic analog input signal fault 208 = Cavitation is critical |  | enum
00203 | [R] | Status.AlarmCode | Grundfos-specific alarm code | 3 = External alarm from DI 24 = Mechanical vibration critical 30 = Change bearings 44 = Undertemperature 46 = External warning (fault 2) from DI 57 = Dry-running state for more than 10s 61 = Water hammer is critical 64 = Overtemperature 76 = Internal communication error 88 = Sensor fault or no sensor attached 131 = Mechanical unbalamce is critical 133 = Generic sensor limit exceeded 152 = Add-on module comm. fault 157 = Real time clock fault 159 = CIM module comm. fault 162 = Sensor supply fault, 24V 165 = Generic analog input signal fault 208 = Cavitation is critical |  | enum
00204 | [R] | Status.SubWarningCode | Grundfos-specific sub-warning code | unsigned |  | enum
00205 | [R] | Status.SubAlarmCode | Grundfos-specific sub-alarm code | unsigned |  | enum
00206.0 | [R] | StatusWarnBits.VibrationCritical | Mechanical vibration is critical, code 24 | 0 = No warning 1 = Warning |  | bool
00206.1 | [R] | StatusWarnBits.ChangeBearings | Change bearings, code 30. Notice! Marked as "RESERVED" in profile manual | 0 = No warning 1 = Warning |  | bool
00206.2 | [R] | StatusWarnBits.DryRunState | Dry running state has occurred for more than 10s, code 57 | 0 = No warning 1 = Warning |  | bool
00206.3 | [R] | StatusWarnBits.SensorFault | Sensor fault or no sensor attached, code 88 | 0 = No warning 1 = Warning |  | bool
00206.4 | [R] | StatusWarnBits.InternalCommFault | Internal communication error, code 76 | 0 = No warning 1 = Warning |  | bool
00206.5 | [R] | StatusWarnBits.CavitationCritical | Cavitation critical, code 208 | 0 = No warning 1 = Warning |  | bool
00206.6 | [R] | StatusWarnBits.Overtemperature | Overtemperature, code 64 | 0 = No warning 1 = Warning |  | bool
00206.7 | [R] | StatusWarnBits.Undertemperature | Undertemperature, code 44 | 0 = No warning 1 = Warning |  | bool
00206.8 | [R] | StatusWarnBits.WaterhammerCritical | Waterhammer is critical, code 61 | 0 = No warning 1 = Warning |  | bool
00206.9 | [R] | StatusWarnBits.UnbalanceCritical | Mechanical unbalance is critical, code 131 | 0 = No warning 1 = Warning |  | bool
00206.10 | [R] | StatusWarnBits.RealTimeClockFault | Real Time Clock fault, code 157, GiM 1.x only | 0 = No warning 1 = Warning |  | bool
00206.11 | [R] | StatusWarnBits.CIMCommFault | CIM module comm. fault, code 159, GiM 1.x only | 0 = No warning 1 = Warning |  | bool
00206.12 | [R] | StatusWarnBits.AddOnModuleCommFault | Add on module comm. fault, code 152, GiM 1.x only | 0 = No warning 1 = Warning |  | bool
00206.13 | [R] | StatusWarnBits.ExternalWarningSignal | External warning signal from digital input, code 46, GiM 1.x only | 0 = No warning 1 = Warning |  | bool
00207.0 | [R] | StatusAlarmBits.VibrationCritical | Mechanical vibration is critical, code 24 | 0 = No alarm 1 = Alarm |  | bool
00207.1 | [R] | StatusAlarmBits.ChangeBearings | Change bearings, code 30. Notice! Marked as "RESERVED" in profile manual | 0 = No alarm 1 = Alarm |  | bool
00207.2 | [R] | StatusAlarmBits.DryRunState | Dry running state has occurred for more than 10s, code 57 | 0 = No alarm 1 = Alarm |  | bool
00207.3 | [R] | StatusAlarmBits.SensorFault | Sensor fault or no sensor attached, code 88 | 0 = No alarm 1 = Alarm |  | bool
00207.4 | [R] | StatusAlarmBits.InternalCommFault | Internal communication error, code 76 | 0 = No alarm 1 = Alarm |  | bool
00207.5 | [R] | StatusAlarmBits.CavitationCritical | Cavitation critical, code 208 | 0 = No alarm 1 = Alarm |  | bool
00207.6 | [R] | StatusAlarmBits.Overtemperature | Overtemperature, code 64 | 0 = No alarm 1 = Alarm |  | bool
00207.7 | [R] | StatusAlarmBits.Undertemperature | Undertemperature, code 44 | 0 = No alarm 1 = Alarm |  | bool
00207.8 | [R] | StatusAlarmBits.WaterhammerCritical | Waterhammer is critical, code 61. | 0 = No alarm 1 = Alarm |  | bool
00207.9 | [R] | StatusAlarmBits.UnbalanceCritical | Mechanical unbalance is critical, code 131 | 0 = No alarm 1 = Alarm |  | bool
00207.10 | [R] | StatusAlarmBits.RealTimeClockFault | Real Time Clock fault, code 157, GiM 1.x only | 0 = No alarm 1 = Alarm |  | bool
00207.11 | [R] | StatusAlarmBits.CIMCommFault | CIM module comm. fault, code 159, GiM 1.x only | 0 = No alarm 1 = Alarm |  | bool
00207.12 | [R] | StatusAlarmBits.AddOnModuleCommFault | Add on module comm. fault, code 152, GiM 1.x only | 0 = No alarm 1 = Alarm |  | bool
00207.13 | [R] | StatusAlarmBits.ExternalAlarmSignal | External alarm signal from digital input, code 3, GiM 1.x only | 0 = No alarm 1 = Alarm |  | bool
00208 | [R] | Status.GiMUnixRtc_HI | Device time and date in UNIX format |  | 1 | s
00209 | [R] | Status.GiMUnixRtc_LO
GiM VTU DATA [R]
00301 | [R] | MeasuredData.MotorSpeed | Motor speed | unsigned | 1 | rpm
00302 | [R] | MeasuredData.LiquidTemp | Temperature of pumped liquid, GiM 0.5 only, RESERVED in manual | unsigned | 0.01 | K
00303 | [R] | MeasuredData.LiquidTempLowLimit | Pumped liquid low limit temperature, GiM 0.5 only, RESERVED in manual | unsigned | 0.01 | K
00304 | [R] | MeasuredData.LiquidTempHighLimit | Pumped liquid high limit temperature. GiM 0.5 only, RESERVED in manual | unsigned | 0.01 | K
00305 | [R] | MeasuredData.Unbalance | Mechanical unbalance level (normalized) | unsigned | 0.01 | mm/s
00306 | [R] | MeasuredData.UnbalanceWarnLimit | Mechanical unbalance level, warning limit | unsigned | 0.01 | mm/s
00307 | [R] | MeasuredData.UnbalanceAlarmLimit | Mechanical unbalance level, alarm limit | unsigned | 0.01 | mm/s
00308 | [R] | MeasuredData.UnbalanceUpperLimit | Mechanical unbalance level, max upper limit (range) | unsigned | 0.01 | mm/s
00309 | [R] | MeasuredData.UnbalanceState | State of mechanical unbalance | 1=Good 2=Warning 3=Alarm 255=Not detectable |  | enum
00310 | [R] | MeasuredData.Cavitation | Cavitation level (normalized) | unsigned | 0.01 | unscaled
00311 | [R] | MeasuredData.CavitationWarnLimit | Cavitation level, warning limit | unsigned | 0.01 | unscaled
00312 | [R] | MeasuredData.CavitationAlarmLimit | Cavitation level, alarm limit | unsigned | 0.01 | unscaled
00313 | [R] | MeasuredData.CavitationUpperLimit | Cavitation level, max upper limit (range) | unsigned | 0.01 | unscaled
00314 | [R] | MeasuredData.CavitationState | State of pump cavitation | 1=Good 2=Warning 3=Alarm 255=Not detectable |  | enum
00315 | [R] | MeasuredData.WaterHammer | Water hammer level (normalized) | unsigned | 0.01 | unscaled
00316 | [R] | MeasuredData.WaterHammerWarnLimit | Water hammer level, warning limit | unsigned | 0.01 | unscaled
00317 | [R] | MeasuredData.WaterHammerAlarmLimit | Water hammer level, alarm limit | unsigned | 0.01 | unscaled
00318 | [R] | MeasuredData.WaterHammerUpperLimit | Water hammer level, max upper limit (range) | unsigned | 0.01 | unscaled
00319 | [R] | MeasuredData.WaterHammerState | State of water hammer | 1=Good 2=Warning 3=Alarm 255=Not detectable |  | enum
00320 | [R] | MeasuredData.BearingWear | Bearing wear (normalized) Notice! Marked as "RESERVED" in profile manual | unsigned | 0.01 | unscaled
00321 | [R] | MeasuredData.BearingWearWarnLimit | Bearing wear, warning limit. Notice! Marked as "RESERVED" in profile manual | unsigned | 0.01 | unscaled
00322 | [R] | MeasuredData.BearingWearAlarmLimit | Bearing wear, alarm limit.Notice! Marked as "RESERVED" in profile manual | unsigned | 0.01 | unscaled
00323 | [R] | MeasuredData.BearingWearUpperLimit | Bearing wear, upper limit (range).Notice! Marked as "RESERVED" in profile manual | unsigned | 0.01 | unscaled
00324 | [R] | MeasuredData.BearingWearState | State of bearing wear. Notice! Marked as "RESERVED" in profile manual | 1=Good 2=Warning 3=Alarm 255=Not detectable |  | enum
00325 | [R] | MeasuredData.AbsVibration | Absolute Overall Vibration level (normalized) | unsigned | 0.01 | mm/s
00326 | [R] | MeasuredData.AbsVibrationWarnLimit | Absolute Overall Vibration level, warning limit | unsigned | 0.01 | mm/s
00327 | [R] | MeasuredData.AbsVibrationAlarmLimit | Absolute Overall Vibration level, alarm limit | unsigned | 0.01 | mm/s
00328 | [R] | MeasuredData.AbsVibrationUpperLimit | Absolute Overall Vibration level, upper limit (range) | unsigned | 0.01 | mm/s
00329 | [R] | MeasuredData.AbsVibrationState | State of Absolute Overall Vibration Level | 1=Good 2=Warning 3=Alarm 255=Not detectable |  | enum
00330 | [R] | MeasuredData.DryRunning | Current status of dry running detection | 0 = Not dry running 1 = Dry running |  | bool
00331 | [R] | MeasuredData.LiquidTemp | Temperature of pumped liquid, GiM 1.x only | signed | 0.1 | °C
00332 | [R] | MeasuredData.LowLiquidTempWarnLimit | Pumped liquid low temperature, warning limit, GiM 1.x only | signed | 0.1 | °C
00333 | [R] | MeasuredData.LowLiquidTempAlarmLimit | Pumped liquid low temperature, alarm limit, GiM 1.x only | signed | 0.1 | °C
00334 | [R] | MeasuredData.LowLiquidTempLowerLimit | Pumped liquid low temperature, min lower limit (range), GiM 1.x only | signed | 0.1 | °C
00335 | [R] | MeasuredData.LowLiquidTempState | State of LowLiquidTemp | 1=Good 2=Warning 3=Alarm 255=Not detectable |  | enum
00336 | [R] | MeasuredData.HighLiquidTempWarnLimit | Pumped liquid high temperature, warning limit, GiM 1.x only | signed | 0.1 | °C
00337 | [R] | MeasuredData.HighLiquidTempAlarmLimit | Pumped liquid high temperature, alarm limit, GiM 1.x only | signed | 0.1 | °C
00338 | [R] | MeasuredData.HighLiquidTempUpperLimit | Pumped liquid high temperature, max upper limit (range), GiM 1.x only | signed | 0.1 | °C
00339 | [R] | MeasuredData.HighLiquidTempState | State of HighLiquidTemp | 1=Good 2=Warning 3=Alarm 255=Not detectable |  | enum
00340 | [R] | MeasuredData.RelVibration | Relative overall vibration level (normalized) | signed | 0.01 | mm/s
00341 | [R] | MeasuredData.RelVibrationWarnLimit | Relative overall vibration level, warning limit | signed | 0.01 | mm/s
00342 | [R] | MeasuredData.RelVibrationState | Relative overall vibration level state | 1=Good 2=Warning 255=Not detectable |  | enum
00360-96 |  | RESERVED
USER REGISTERS [R/W]
00751 | [R/W] | UserLabel1 |  |  |  | unscaled
00752 | [R/W] | UserLabel2 |  |  |  | unscaled
00753 | [R/W] | UserLabel3 |  |  |  | unscaled
00754-00799 | [R/W] | UserLabel4-UserLabel49 |  |  |  | unscaled
00800 | [R/W] | UserLabel50 |  |  |  | unscaled
GiM I/O Board
G i M I / O B O A R D C O N T R O L
01202-01210
G i M I / O B O A R D C O N F I G U R A T I O N
01211.0 | [W] | GiMIO.SetLimit1ExceededED | Configuration of Limit 1 exceeded function E/D, 1= Enabled | 0 = Disable 1 = Enable |  | bool
01211.1 | [W] | GiMIO.SetLimit2ExceededED | Configuration of Limit 2 exceeded function E/D, 1= Enabled | 0 = Disable 1 = Enable |  | bool
01211.2 | [W] | GiMIO.SetLimit3ExceededED | Configuration of Limit 3 exceeded function E/D, 1= Enabled | 0 = Disable 1 = Enable |  | bool
01211.3 | [W] | GiMIO.SetLimit4ExceededED | Configuration of Limit 4 exceeded function E/D, 1= Enabled | 0 = Disable 1 = Enable |  | bool
01211.4 | [W] | GiMIO.SetLimit5ExceededED | Configuration of Limit 5 exceeded function E/D, 1= Enabled | 0 = Disable 1 = Enable |  | bool
01211.5 | [W] | GiMIO.SetLimit6ExceededED | Configuration of Limit 6 exceeded function E/D, 1= Enabled | 0 = Disable 1 = Enable |  | bool
01211.6 | [W] | GiMIO.SetLimit7ExceededED | Configuration of Limit 7 exceeded function E/D, 1= Enabled | 0 = Disable 1 = Enable |  | bool
01211.7 | [W] | GiMIO.SetLimit8ExceededED | Configuration of Limit 8 exceeded function E/D, 1= Enabled | 0 = Disable 1 = Enable |  | bool
01212-01220
G i M I / O B O A R D C O N F I G U R A T I O N S T A T U S
01221.0 | [R] | GiMIO.Limit1ExceededED | Status of Limit 1 exceeded function E/D, 1= Enabled | 0 = Disabled 1 = Enabled |  | bool
01221.1 | [R] | GiMIO.Limit2ExceededED | Status of Limit 2 exceeded function E/D, 1= Enabled | 0 = Disabled 1 = Enabled |  | bool
01221.2 | [R] | GiMIO.Limit3ExceededED | Status of Limit 3 exceeded function E/D, 1= Enabled | 0 = Disabled 1 = Enabled |  | bool
01221.3 | [R] | GiMIO.Limit4ExceededED | Status of Limit 4 exceeded function E/D, 1= Enabled | 0 = Disabled 1 = Enabled |  | bool
01221.4 | [R] | GiMIO.Limit5ExceededED | Status of Limit 5 exceeded function E/D, 1= Enabled | 0 = Disabled 1 = Enabled |  | bool
01221.5 | [R] | GiMIO.Limit6ExceededED | Status of Limit 6 exceeded function E/D, 1= Enabled | 0 = Disabled 1 = Enabled |  | bool
01221.6 | [R] | GiMIO.Limit7ExceededED | Status of Limit 7 exceeded function E/D, 1= Enabled | 0 = Disabled 1 = Enabled |  | bool
01221.7 | [R] | GiMIO.Limit8ExceededED | Status of Limit 8 exceeded function E/D, 1= Enabled | 0 = Disabled 1 = Enabled |  | bool
01222-01230
G i M I / O B O A R D E V E N T S T A T U S
01231.0 | [R] | GiMIO.Limit1Exceeded | Limit 1 exceeded (Code 133.1001) | 0 = No event 1 = Event active |  | bool
01231.1 | [R] | GiMIO.Limit2Exceeded | Limit 2 exceeded (Code 133.1002) | 0 = No event 1 = Event active |  | bool
01231.2 | [R] | GiMIO.Limit3Exceeded | Limit 3 exceeded (Code 133.1003) | 0 = No event 1 = Event active |  | bool
01231.3 | [R] | GiMIO.Limit4Exceeded | Limit 4 exceeded (Code 133.1004) | 0 = No event 1 = Event active |  | bool
01231.4 | [R] | GiMIO.Limit5Exceeded | Limit 5 exceeded (Code 133.1005) | 0 = No event 1 = Event active |  | bool
01231.5 | [R] | GiMIO.Limit6Exceeded | Limit 6 exceeded (Code 133.1006) | 0 = No event 1 = Event active |  | bool
01231.6 | [R] | GiMIO.Limit7Exceeded | Limit 7 exceeded (Code 133.1007) | 0 = No event 1 = Event active |  | bool
01231.7 | [R] | GiMIO.Limit8Exceeded | Limit 8 exceeded (Code 133.1008) | 0 = No event 1 = Event active |  | bool
01232.0 | [R] | GiMIO.AnalogIn1OutOfRange | Analog Input 1 outside range (Code 165.1001) | 0 = No event 1 = Event active |  | bool
01232.1 | [R] | GiMIO.AnalogIn2OutOfRange | Analog Input 2 outside range (Code 165.1002) | 0 = No event 1 = Event active |  | bool
01232.2 | [R] | GiMIO.AnalogIn3OutOfRange | Analog Input 3 outside range (Code 165.1003) | 0 = No event 1 = Event active |  | bool
01233.0 | [R] | GiMIO.24V1OutOfRange | 24V output 1 outside range (Code 162.1001) | 0 = No event 1 = Event active |  | bool
01233.1 | [R] | GiMIO.24V2OutOfRange | 24V output 2 outside range (Code 162.1002) | 0 = No event 1 = Event active |  | bool
01233.2 | [R] | GiMIO.24V3OutOfRange | 24V output 3 outside range (Code 162.1003) | 0 = No event 1 = Event active |  | bool
01234.0 | [R] | GiMIO.PtSensorOutOfRange | PT temperature sensor, outside range or no sensor attached (Code 165.2001) | 0 = No event 1 = Event active |  | bool
01235-01240 | [R]
G i M I / O B O A R D B O A R D D I G I T A L S T A T U S
01241.0 | [R] | GiMIO.DigitalInput | DI, Digital input (fixed) | 0 = In-active 1 = Active |  | bool
01242.0 | [R] | GiMIO.RelayOutput | DO, Digital output status (fixed relay output) | 0 = In-active 1 = Active |  | bool
01243-50 | [R]
G i M I / O B O A R D S E N S O R M E A S U R E M E N T S
01251 | [R] | GiMIO.AnalogInput1Scaled | AI1, Analog input 1 scaled | signed |  | unit
01252 | [R] | GiMIO.AnalogInput1Relative | AI1, Analog input 1 relative to range | signed | 0.01 | %
01253 | [R] | GiMIO.AnalogInput1Unit | AI1, Analog input 1 scaling unit | 20 = 0.1 oC 22 = 0.1 m3/h 27 = 0.01 bar 83 = 0.01 m 107 = 0.01 % 110 = 0.01 oC 255 = NA |  | enum
01254 | [R] | GiMIO.AnalogInput1Min | AI1, Analog input 1 scaling range minimum value | signed |  | unit
01255 | [R] | GiMIO.AnalogInput1Max | AI1, Analog input 1 scaling range maximum value | signed |  | unit
01256 | [R] | GiMIO.AnalogInput2Scaled | AI2, Analog input 2 scaled | signed |  | unit
01257 | [R] | GiMIO.AnalogInput2Relative | AI2, Analog input 2 relative to range | signed | 0.01 | %
01258 | [R] | GiMIO.AnalogInput2Unit | AI2, Analog input 2 scaling unit | 20 = 0.1 oC 22 = 0.1 m3/h 27 = 0.01 bar 83 = 0.01 m 107 = 0.01 % 110 = 0.01 oC 255 = NA |  | enum
01259 | [R] | GiMIO.AnalogInput2Min | AI2, Analog input 2 scaling range minimum value | signed |  | unit
01260 | [R] | GiMIO.AnalogInput2Max | AI2, Analog input 2 scaling range maximum value | signed |  | unit
01261 | [R] | GiMIO.AnalogInput3Scaled | AI3, Analog input 3 scaled | signed |  | unit
01262 | [R] | GiMIO.AnalogInput3Relative | AI3, Analog input 3 relative to range | signed | 0.01 | %
01263 | [R] | GiMIO.AnalogInput3Unit | AI3, Analog input 3 scaling unit | 20 = 0.1 oC 22 = 0.1 m3/h 27 = 0.01 bar 83 = 0.01 m 107 = 0.01 % 110 = 0.01 oC 255 = NA |  | enum
01264 | [R] | GiMIO.AnalogInput3Min | AI3, Analog input 3 scaling range minimum value | signed |  | unit
01265 | [R] | GiMIO.AnalogInput3Max | AI3, Analog input 3 scaling range maximum value | signed |  | unit
01266 | [R] | GiMIO .TemperatureInput | PT1, Temperature input 1 (PT100/PT1000 configurable), [-50; 250 °C] | signed | 0.1 | °C
01267-70 | [R]
G i M I / O B O A R D S E N S O R S M A P P E D T O P A R A M E T E R S
01271 | [R] | GiMIO.InletPressure | Pump inlet pressure, [-1; 120 bar] | signed | 0.01 | bar
01272 | [R] | GiMIO.InletDiffPressure | Pump inlet differential pressure, [-10; 10 bar] | signed | 0.01 | bar
01273 | [R] | GiMIO.OutletPressure | Pump outlet pressure, [0; 120 bar] | signed | 0.01 | bar
01274 | [R] | GiMIO.OutletDiffPressure | Pump outlet differential pressure, [-10; 10 bar] | signed | 0.01 | bar
01275 | [R] | GiMIO.DiffPressure | Pump differential pressure, head, [-120; 120 bar] | signed | 0.01 | bar
01276 | [R] | GiMIO.RemotePressure1 | Remote pressure 1, [-1; 120 bar] | signed | 0.01 | bar
01277 | [R] | GiMIO.RemotePressure2 | Remote pressure 2, [-1; 120 bar] | signed | 0.01 | bar
01278 | [R] | GiMIO.RemoteDiffPressure | Remote differential pressure, [-120; 120 bar] | signed | 0.01 | bar
01279 | [R] | GiMIO.TankLevelEmptying | Tank level, emptying (feed tank level), [0; 10 m] | unsigned | 0.001 | m
01280 | [R] | GiMIO.TankLevelFilling | Tank level, filling (storage tank level), [0; 10 m] | unsigned | 0.001 | m
01281 | [R] | GiMIO.PumpFlow | Pump flow, [0; 600 m3/h] | unsigned | 0.01 | m3/h
01282 | [R] | GiMIO.RemoteFlow | Remote flow, [0; 600 m3/h] | unsigned | 0.01 | m3/h
01283 | [R] | GiMIO.LiquidTemperature | Pumped liquid temperature, [-50; 250 °C] | signed | 0.1 | °C
01284 | [R] | GiMIO.RemoteLiquidTemperature1 | Remote liquid temperature 1, [-50; 250 °C] | signed | 0.1 | °C
01285 | [R] | GiMIO.RemoteLiquidTemperature2 | Remote liquid temperature 2, [-50; 250 °C] | signed | 0.1 | °C
01286 | [R] | GiMIO.RemoteLiquidDiffTemperature | Remote liquid differential temperature, [-100; 250 °C] | signed | 0.1 | °C
01287 | [R] | GiMIO.AmbientTemperatureOutdoor | Ambient temperature, outdoor, [-50; 100 °C] | signed | 0.1 | °C
01288 | [R] | GiMIO.AmbientTemperatureRoom | Ambient temperature, room, [-50; 100 °C] | signed | 0.1 | °C
01289 | [R] | GiMIO.BearingTemperatureDE | Bearing temperature, Drive End, [-50; 250 °C] | signed | 0.1 | °C
01290 | [R] | GiMIO.BearingTemperatureNDE | Bearing temperature, Non-Drive End, [-50; 250 °C] | signed | 0.1 | °C
01291 | [R] | GiMIO.AuxSensorInput | Auxilary sensor input, [0; 100 %] | signed | 0.01 | %
01292 | [R] | GiMIO.RemoteTemperature1 | Remote temperature 1, [-50; 250 °C] | signed | 0.1 | °C
01293 | [R] | GiMIO.RemoteTemperature2 | Remote temperature 2, [-50; 250 °C] | signed | 0.1 | °C
01294 | [R] | GiMIO.RemoteDiffTemperature | Remote differential temperature, [-100; 250 °C] | signed | 0.1 | °C
RESERVED REGISTERS FOR ENGINEERING [R/W]
64001
:
65000

## Pump
GRUNDFOS CIM 200/260/500 and SoftCIM MODBUS profile for pumps
All addresses are registers (16 bit), and the address is written in decimal format.
Sheet version: 02.07.12
Change date (d-m-y): 20-05-2025
Reg. addr. | Access | Modbus parameter name | Description | Bool/Enum description | Modbus Scale | Modbus Unit | Modbus Offset | HM2000 | HM3000 | HM3000 Midlife | HM Large | MGE H/I/J/K | CUE | Magna | MAGNA3 | LaUPE / DAB
DEVICE CONFIG [R/W] - All saved in EEPROM
00001 | [R/W] | Config.SlaveMinimumReplyDelay | For adding a reply delay in ms (used with radio modem) |  | 1 | ms |  | x | x | x | x | x | x | x | x | x
00002 | [R/W] | RESERVED | [13 empty] | x
00003 | [R/W] | Config.SoftwareDefinedModbusAddress | Set a Modbus slave address to use if the address switches are set to an invalid value (Modbus RTU only). |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00004 | [R/W] | Config.ModbusBitRate | If set to software defined, use this bit rate (Modbus RTU only). | 0 = 1200 1 = 2400 2 = 4800 3 = 9600 4 = 19200 5 = 38400 |  | enum |  | x | x | x | x | x | x | x | x | x
00005 | [R/W] | Config.AutoAckControlBits | Acknowlege behaviour of control bits | 0 = Manual, 1 = Automatic |  | bool |  | x | x | x | x | x | x | x | x | x
00006 |  | RESERVED
00007 | [R/W] | Config.ScadaCallbackRegister | Register in the master used for unsolicited messages. (CIM 260 only) |  |  | unscaled
00008 | [R/W] | Config.NoDataActivityTimeout | The elapsed time with no data activity before the module issues a "Data connection restart". (CIM 260 only) |  | 1 | min
00009 | [R/W] | Config.SoftwareDefinedParity | If software defined, use this parity setting (Modbus RTU only). | 0 = No parity 1 = Even parity 2 = Odd parity |  | enum |  | x | x | x | x | x | x | x | x | x
00010 | [R/W] | Config.SoftwareDefinedStopBit | If software defined, use this stop bit setting (Modbus RTU only). | 0 = Not defined 1 = 1 stop bit 2 = 2 stop bit |  | enum |  | x | x | x | x | x | x | x | x
00011 | [R/W] | Config.ScadaPinCode | Code to use if ScadaPinCode is enabled (CIM 260 only) |  |  |  |  | x | x | x | x | x | x | x | x
00012 | [R/W] | Config.Watchdog | Saved in EEPROM. Default = 0 (Disabled). Values 1-4 will set value=5. Values >3600 will set value=3600. Only for CIM 200 and CIM 500 |  | 1 | s |  | x | x | x | x | x | x | x | x
00013 | [R/W] | Config.GENIbusDiodeOff | Switching off the CIM 200 GENIbus diode (LED2) | 0=On (default) 1=Off |  | bool |  | x | x | x | x | x | x | x | x
DEVICE STATUS [R]
00021 | [R] | GENIbusCRCErrorCnt | CRC error counter on GENIbus |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00022 | [R] | GENIbusDataErrorCnt | Data error counter on GENIbus |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00023 | [R] | VersionNumber | CIM module software version number (BCD digits 1-4) |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00024 | [R] | ActualModbusAddress | Actual modbus slave address (Read only) |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00025 | [R] | GENIbusTXcount HI | Transmit counter on GENIbus |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00026 | [R] | GENIbusTXcount LO | [5 empty] | x | x | x | x | x | x | x | x | x
00027 | [R] | GENIbusRXcount HI | Receive counter on GENIbus |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00028 | [R] | GENIbusRXcount LO | [5 empty] | x | x | x | x | x | x | x | x | x
00029.0 | [R] | ScadaPinCodeEnabled | Determines if the use of a Scada Pin Code is enabled (CIM 260 only) | 0 = Pin code disabled 1 = Pin code enabled |  |  |  | x | x | x | x | x | x | x | x | x
00029.1 | [R] | WriteAccessStatus | Determines if write (control) access is granted or not (CIM 260 only) | 0 = No write access 1 = Write access
00029.2 | [R] | LockinBlocked | Login blocked due to too many password attempts (CIM 260 only) | 0 = No Login blocking 1 = Login blocked
00030 | [R] | GrundfosUnitFamily | Grundfos product family | 0 = - 1 = MAGNA series 2 = MGE series 7 = Motor Protection Unit 17 = Multi-E booster 21 = MPC / Multi-B 25 = CR Monitor 26 = Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller CU 2X1 48 = Level controller LC 2x1 65 = SQ Controller CU 202/302 255 = N/A |  | enum |  | x | x | x | x | x | x | x | x | x
00031 | [R] | GrundfosUnitType | Grundfos product type number |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00032 | [R] | GrundfosUnitVersion | Grundfos product version number |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00033 | [R] | BatteryState | State of cellular module battery (CIM 260 only) | 0 = Battery not present 1 = Battery must be replaced 2 = Battery charging 3 = Battery needs charging, but temperature too high 4 = Battery needs charging, but temperature too low 5 = Battery Low 6 = Battery OK 255 = Battery state not available |  | enum |  | x | x | x | x | x | x | x | x
00034 | [R] | ProductSoftwareVersionHI | Product software version (BCD digit 1-4 aa.bb) |  |  | BCD number | [5 empty] | x |  |  | x
00035 | [R] | ProductSoftwareVersionLO | Product software version (BCD digit 5-8 cc.dd) |  |  | BCD number | [5 empty] | x |  |  | x
00036 | [R] | ProductSoftwareDayMonth | Product software date (BCD ddmm) |  |  | BCD number | [5 empty] | x |  |  | x
00037 | [R] | ProductSoftwareYear | Product software date (BCD yyyy) |  |  | BCD number | [5 empty] | x |  |  | x
CIM 260 REAL TIME CLOCK [R/W] CIM 260 ONLY (not described in profile manual) | [15 empty] | x
00080 | [W] | SetUNIXRealTimeClockHI | Set cellular Real Time Clock (32 bit UNIX format) (CIM 260 only) |  | 1 | s |  | x | x | x | x | x | x | x | x | x
00081 | [W] | SetUNIXRealTimeClockLO | [5 empty] | x | x | x | x | x | x | x | x | x
00082 | [W] | SetRtcSecond | Set cellular Real Time Clock (Seconds) (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00083 | [W] | SetRtcMinute | Set cellular Real Time Clock (Minutes) (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00084 | [W] | SetRtcHour | Set cellular Real Time Clock (Hours) (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00085 | [W] | SetRtcDay | Set cellular Real Time Clock (Day) (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00086 | [W] | SetRtcMonth | Set cellular Real Time Clock (Month) (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00087 | [W] | SetRtcYear | Set cellular Real Time Clock (Year - after 2000) (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00088.0 | [W] | SetRtc | Set cellular Real Time Clock (Normal format) (CIM 260 only) | 0 = No command 1 = Set the clock |  | bool |  | x | x | x | x | x | x | x | x | x
00089 | [R] | Status.UNIXRealTimeClockHI | cellular Real Time Clock (32 bit UNIX format) (CIM 260 only) |  | 1 | s |  | x | x | x | x | x | x | x | x | x
00090 | [R] | Status.UNIXRealTimeClockLO | [5 empty] | x | x | x | x | x | x | x | x | x
00091 | [R] | Status.RtcSecond | Cellular Real Time Clock - Seconds (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00092 | [R] | Status.RtcMinute | Cellular Real Time Clock - Minutes (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00093 | [R] | Status.RtcHour | Cellular Real Time Clock - Hours (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00094 | [R] | Status.RtcDay | Cellular Real Time Clock - Day of month (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00095 | [R] | Status.RtcMonth | Cellular Real Time Clock - Month (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00096 | [R] | Status.RtcYear | Cellular Real Time Clock - Year (after 2000) (CIM 260 only) |  |  | enum |  | x | x | x | x | x | x | x | x | x
00097.0 | [R] | Status.AcknowledgeSetRTC | Acknowledge of celular Set Real Time Clock (CIM 260 only) | 0 = No acknowledge 1 = Acknowledged |  | bool |  | x | x | x | x | x | x | x | x
PUMP CONTROL [W]
00101.5 | [W] | Control.EnableMaxFlowLimit | Enables the MAX flow limit | 0 = Disabled 1 = Enabled |  | bool | [5 empty] | x |  |  | x
00101.4 | [W] | Control.CopyToLocal | Copies local settings to remote settings | 0 = Don't copy 1 = Copy to Local |  | bool |  |  |  | x | x | x | x |  | x
00101.3 |  | RESERVED | [13 empty] | x
00101.2 | [W] | Control.ResetAlarm | Resets alarms and warnings | 0 = No resetting 1 = Reset alarm |  | bool |  | x | x | x | x | x | x | x | x | x x
00101.1 | [W] | Control.OnOffReq | Set the pump on or off | 0 = Off 1 = On |  | bool |  | x x | x x | x x | x x | x x | x x | x x | x x | x x
00101.0 | [W] | Control.RemoteAccessReq | Set local or remote (bus) control | 0 = Local control 1 = Remote control (bus) |  | bool |  | x x | x x | x x | x x | x x | x x | x x | x x | x x x - - x - - - x - -
00102 | [W] | Control.ControlMode | Set control mode | 0 = Constant speed 1 = Constant frequency 3 = Constant head 4 = Constant pressure 5 = Constant diff. pressure 6 = Proportional pressure 7 = Constant flow 8 = Constant temperature 9 = Constant diff. temp. 10 = Constant level 128 = AUTOADAPT (PP) 129 = FLOWADAPT 130 = Closed loop sensor 131 = AUTOADAPT (CP) |  | enum |  | x x x x - x - - - - x - - | x x x x - x - - - - x - - | x x x x - x - - - - x - - | x x x x - x - - - - x - - | x x x x x x x x x x x x x | x x x x - x - - - - - - - | x x x x - x - - - - x - - | x x x x x x - x - - x x - | x x x
00103 | [W] | Control.OperationMode | Set operating mode | 0 = AutoControl (Normal) 4 = OpenLoopMinimum 6 = OpenLoopMaximum |  | enum |  | x x x | x x x | x x x | x x x | x x x | x x x | x x x | x x x | x
00104 | [W] | Control.Setpoint | Set the setpoint in 0.01% |  | 0.01 | % |  | x | x | x | x | x | x | x | x
00105.0 | [W] | Control.Relay1Control | Control of relay 1 (E-Pumps and CUE only) | 0 = Closed 1 = Open |  | bool |  | x x | x x | x x | x x | x x | x x
00105.1 | [W] | Control.Relay2Control | Control of relay 2 (Large MGE, MGE H/I/J/K and CUE only) | 0 = Closed 1 = Open |  | bool |  |  |  |  | x x | x x | x x
00105.2 | [W] | Control.Relay3Control | Control of relay 3 (MGE H/I/J/K) | 0 = Closed 1 = Open |  | bool | [5 empty] | x x
00105.3 | [W] | Control.Relay4Control | Control of relay 4 (MGE H/I/J/K) | 0 = Closed 1 = Open |  | bool | [5 empty] | x x
00106 | [W] | Control.SetMaxFlowLimit | Maximum flow limit |  | 0.01 | m3/h | [5 empty] | x x |  |  | x x
00107 | [W] | Control.SetPumpUnixRtc HI | Real Time Clock (32 bit UNIX format) |  | 1 | s | [5 empty] | x x |  |  | x x
00108 | [W] | Control.SetPumpUnixRtc LO | [9 empty] | x x |  |  | x x
00109 | [W] | Control.SensorFeedback | Sensor feedback via fieldbus |  | 0.01 | % | [5 empty] | x x |  |  | x x
00110 | [W] | Control.SetKp | Setting of proportional gain, Kp |  | 0.1 | [6 empty] | x x |  |  | x x
00111 | [W] | Control.SetTi | Setting of integral action time, Ti |  | 0.1 | s | [5 empty] | x x |  |  | x x
00112 | [W] | Control.SetDirectCtr | Selection of Direct/Inverse control | 0 = Inverse control 1 = Direct control | 0 | bool | [5 empty] | x x |  |  | x x
PUMP STATUS [R] | [15 empty] | -
00201.15 | [R] | Status.AtMinSpeed | Running at minimum speed | 0 = No 1 = Yes |  | bool |  | x | x | x | x | x | x | x | x
00201.14 | [R] | [14 empty] | -
00201.13 | [R] | Status.AtMaxSpeed | Running at maximum speed | 0 = No 1 = Yes |  | bool |  | x | x | x | x | x | x | x | x
00201.12 | [R] | Status.ForcedToLocal | State of the "Forced to local" control option | 0 = Not forced to local 1 = Forced to local |  | bool | [5 empty] | x |  |  | x
00201.11 | [R] | Status.Warning | Warning present | 0 = No 1 = Yes |  | bool |  | x | x | x | x | x | x |  | x | x
00201.10 | [R] | Status.AlarmCode | Alarm present | 0 = No 1 = Yes |  | bool |  | x | x | x | x | x | x | x | x | x
00201.9 | [R] | Status.OnOff | On/Off status of pump | 0 = Off 1 = On |  | bool |  | x | x | x | x | x | x | x | x | x
00201.8 | [R] | Status.AccessMode | Access Mode status | 0 = Local control 1 = Remote control (bus) |  | bool |  | x | x | x | x | x | x | x | x
00201.7 | [R] | Status.Direction | Direction status | 0 = ClockWise (Seen from ventilator) 1 = CounterClockWise (Seen from ventilator) |  | bool |  | x | x | x | x | x | x |  | x | x
00201.6 | [R] | Status.Rotation | Rotational status | 0 = No rotation 1 = Rotation |  | bool |  | x | x | x | x | x | x | x | x
00201.5 | [R] | Status.AtMaxPower | Running at power limit | 0 = No 1 = Yes |  | bool | [5 empty] | x |  |  | x | x
00201.4 | [R] | Status.SetpointInfluence | Setpoint influence status | 0 = No influence 1 = Setpoint influence active |  | bool | [5 empty] | x |  | x | x | x
00201.3 | [R] | Status.ResetAlarmAck | Acknowledge of ResetAlarm | 0 = No acknowledge 1 = Acknowledged |  | bool |  | x | x | x | x | x | x | x | x
00201.2 | [R] | Status.EnableMaxFlowLimit | Enable/Disable status on MAX flow limit | 0 = Disabled 1 = Enabled |  | bool | [5 empty] | x |  |  | x
00201.1 | [R] | Status.CopyToLocal | Copies remote settings to local settings | 0 = Disabled 1 = Enabled |  | bool | [5 empty] | x |  |  | x
00201.0 | [R] | Status.LowFlowStop | State of "Low Flow Stop" function | 0 = Low Flow Stop not activated 1 = Low Flow Stop activated |  | bool | [5 empty] | x |  |  | x | x
00202 | [R] | Status.ProcessFeedback | Process value (feedback) |  | 0.01 | % |  | x | x | x | x | x | x | x | x | x
00203 | [R] | Status.ControlMode | Actual control mode | 0 = Constant speed 1 = Constant frequency 3 = Constant head 4 = Constant pressure 5 = Constant diff. pressure 6 = Proportional pressure 7 = Constant flow 8 = Constant temperature 9 = Constant diff. temp. 10 = Constant level 128 = AUTOADAPT 129 = FLOWADAPT 130 = Closed loop sensor |  | enum |  | x | x | x | x | x | x | x | x | x x x -
00204 | [R] | Status.OperationMode | Actual operating mode | 0 = AutoControl (Normal) 4 = OpenLoopMinimum 6 = OpenLoopMaximum 7 = UserCurve 8 = StopButton 9 = HandMode) |  | enum |  | x x x - - - | x x x - - - | x x x - - - | x x x - - - | x x x x x x | x x x - x - | x x x - - - | x x x - - - | x
00205 | [R] | Status.AlarmCode | Grundfos-specific alarm code |  |  | enum |  | x | x | x | x | x | x | x | x
00206 | [R] | Status.WarningCode | Grundfos-specific warning code |  |  | enum |  | x | x | x | x | x | x |  | x
00207.0-7 | [R] | Status.MonthsToBearingService | Time to bearing service |  | 1 | months |  |  |  | x | x | x | x
00207.8 | [R] | Status.BearingServiceType | Type of next bearing service | 0 = Lubricate bearings 1 = Change bearings |  | bool |  |  |  | x | x | x | x
00208 | [R] | Status.DriveState | 0 = Stopped, 1 = Accelerating, 2 = Decelerating, 3 = Steady state CL, 4 = - 5 = Accelerating halt, 6 = Decelerating halt, 7 = Start on the run | 0 = Stopped 1 = Accelerating 2 = Decelerating 3 = Steady state CL 4 = - 5 = Accelerating halt 6 = Decelerating halt 7 = Start on the run 255 = NA |  | enum |  |  |  | x | x | x | x
00209 | [R] | Status.FeedBackSensorUnit | Unit of feed back sensor | 0 = bar 1 = mbar 2 = m 3 = kPa 4 = psi 5 = ft 6 = m3/h 7 = m3/s 8 = ltr/s 9 = gpm 10 = C 11 = F 12 = % 13 = Kelvin 14 = ltr/h 255 = NA |  | enum |  | x | x | x | x | x | x |  | x
00210 | [R] | Status.FeedBackSensorMin | Minimum of feedback sensor |  | 1 | unit |  | x | x | x | x | x | x |  | x
00211 | [R] | Status.FeedBackSensorMax | Maximum of feedback sensor |  | 1 | unit |  | x | x | x | x | x | x |  | x
00212 | [R] | Status.NomFrequency | Nominal pump frequency |  | 0.1 | Hz | [5 empty] | x |  |  | x
00213 | [R] | Status.MinFrequency | Minimum pump frequency in % of nominal frequency |  | 0.01 | % | [5 empty] | x |  |  | x
00214 | [R] | Status.MaxFrequency | Maximum pump frequency in % of nominal frequency |  | 0.01 | % | [5 empty] | x |  |  | x
00215 | [R] | Status.SetpointRangeMin | Minimum value of setpoint range in % of sensor max value |  | 0.01 | % | [5 empty] | x |  |  | x
00216 | [R] | Status.SetpointRangeMax | Maximum value of setpoint range in % of sensor max value |  | 0.01 | % | [5 empty] | x |  |  | x
00217 | [R] | Status.MaxPressureRange | Maximum value of head/pressure range |  | 0.01 | bar
00218 | [R] | Status.MaxFlowRange | Maximum value of flow range |  | 0.1 | m3/h
00219 | [R] | Status.MaxPowerRange | Maximum value of power range |  | 1 | W
00220 | [R] | Status.MaxVoltageRange | Maximum value of voltage range |  | 1 | V
00221 | [R] | Status.FlowEstimationState | State of the flow estimation | 0 = Flow estimation within range 1 = Flow estimation below range 2 = Flow estimation above range |  | enum | [5 empty] | x |  |  | x
00222 | [R] | Status.Kp | Status of the proportional gain, Kp |  | 0.1 | [6 empty] | x |  |  | x
00223 | [R] | Status.Ti | Status of the integral action time, Ti |  | 0.1 | s | [5 empty] | x |  |  | x
00224 | [R] | Status.DirectCtr | Status of Direct/Inverse control selection | 0 = Inverse control 1 = Direct control |  | bool | [5 empty] | x |  |  | x
00225 | [R] | Status.ControlSource | What source is in control | 1 = Display 2 = Bus 3 = Handheld 4 = Digital in 5 = ON/OFF button |  | enum | [5 empty] | x |  |  | x
PUMP DATA [R]
00301 | [R] | MeasuredData.Head | Actual head |  | 0.001 | bar |  | xs | xs | xs | xs | xs | xs | x | x | x
00302 | [R] | MeasuredData.VolumeFlow | Actual system flow |  | 0.1 | m³/h |  | xs | xs | xs | xs | xs | xs | x | x | x
00303 | [R] | MeasuredData.RelativePerformance | Performance relative to max |  | 0.01 | % |  | x | x | x | x | x | x | x | x | x
00304 | [R] | MeasuredData.Speed | Actual speed |  | 1 | rpm |  | x | x | x | x | x | x | x | x | x
00305 | [R] | MeasuredData.Frequency | Actual frequency |  | 0.1 | Hz |  | x | x | x | x | x | x | x | x | x
00306 | [R] | MeasuredData.DigitalInput | Digital inputs |  |  | unscaled |  | x | x | x | x | x | x |  | x
00307 | [R] | MeasuredData.DigitalOutput | Digital outputs |  |  | unscaled |  | x | x | x | x | x | x |  | x
00308 | [R] | MeasuredData.ActualSetpoint | Actual setpoint in % of feedback sensor max value |  | 0.01 | % |  | x | x | x | x | x | x | x | x | x
00309 | [R] | MeasuredData.MotorCurrent | Motor current |  | 0.1 | A |  | x | x | x | x | x | x |  | x
00310 | [R] | MeasuredData.DCLinkVoltage | DC Link Voltage |  | 0.1 | V |  | x | x | x | x | x | x | x | x | x
00311 | [R] | MeasuredData.MotorVoltage | Motor voltage |  | 0.1 | V |  | x | x | x | x | x | x
00312 | [R] | MeasuredData.Power HI | Total power consumption |  | 1 | W |  | x | x | x | x | x | x | x | x | x
00313 | [R] | MeasuredData.Power LO | [5 empty] | x | x | x | x | x | x | x | x | x
00314 | [R] | MeasuredData.RemoteFlow | Measured flow at remote sensor |  | 0.1 | m³/h |  |  |  | xs | xs | xs | xs
00315 | [R] | MeasuredData.InletPressure | System inlet pressure relative to atmospheric pressure |  | 0.001 | bar | 1000 |  |  | xs | xs | xs | xs
00316 | [R] | MeasuredData.RemotePressure1 | Measured pressure at external sensor relative to atmospheric pressure |  | 0.001 | bar |  |  |  | xs | xs | xs | xs |  | xs
00317 | [R] | MeasuredData.Feed Tank Level | Feed tank level |  | 0.01 | m | 10000 | xs | xs | xs | xs | xs | xs
00318 | [R] | MeasuredData.PowerElectronicTemp | Temperature of power electronics |  | 0.01 | K |  | x | x | x | x | x | x |  | x
00319 | [R] | MeasuredData.MotorTemp | Temperature of motor |  | 0.01 | K |  |  |  | x | x | x | x
00320 | [R] | MeasuredData.RemoteTemp1 | Temperature at external sensor |  | 0.01 | K |  | xs | xs | xs | xs | xs | xs
00321 | [R] | MeasuredData.ElectronicTemp | Electronics temperature |  | 0.01 | K |  |  |  | - | x | x | x |  | x
00322 | [R] | MeasuredData.PumpLiquidTemp | Temperature of the pumped liquid |  | 0.01 | K |  |  |  | xs | xs | xs | xs | x | x | x
00323 | [R] | MeasuredData.BearingTempDE | Bearing temperature (Drive-End) |  | 0.01 | K |  |  |  | - | x | xs | x
00324 | [R] | MeasuredData.BearingTempNDE | Bearing temperature (Non-Drive-End) |  | 0.01 | K |  |  |  | - | x | xs | x
00325 | [R] | MeasuredData.AuxSensorInput | Auxilary sensor input |  | 0.01 | % |  | xs | xs | xs | xs | xs | xs
00326 | [R] | MeasuredData.SpecificEnergyConsumption | Specific energy consumption |  | 1 | Wh/m3 |  | - | - | - | - | xs | x |  | x
00327 | [R] | MeasuredData.OperationTime HI | Total operating time |  | 1 | h |  | x | x | x | x | x | x | x | x | x
00328 | [R] | MeasuredData.OperationTime LO | [5 empty] | x | x | x | x | x | x | x | x | x
00329 | [R] | MeasuredData.TotalPoweredTime HI | Total powered time |  | 1 | h |  | x | x | x | x | x | x | x | x
00330 | [R] | MeasuredData.TotalPoweredTime LO | [5 empty] | x | x | x | x | x | x | x | x
00331 | [R] | MeasuredData.Torque | Torque |  | 0.1 | Nm |  |  | x | x | x | x | x
00332 | [R] | MeasuredData.Energy HI | Total energy consumption |  | 1 | kWh |  | x | x | x | x | x | x | x | x | x
00333 | [R] | MeasuredData.Energy LO | [5 empty] | x | x | x | x | x | x | x | x | x
00334 | [R] | MeasuredData.NumberOfStarts HI | Number of starts |  | 1 | starts |  | x | x | x | x | x | x |  | x
00335 | [R] | MeasuredData.NumberOfStarts LO | [5 empty] | x | x | x | x | x | x |  | x
00336 | [R] | MeasuredData.Volume | Volume (CUE and MGE H/I only) |  | 0.01 | m³ | [5 empty] | xs | x |  | x
00337 | [R] | MeasuredData.RemoteTemp2 | Temperature at external temperature sensor 2 |  | 0.01 | K | [5 empty] | xs |  |  | xs
00338 | [R] | MeasuredData.UserSetpoint | User selected setpoint (0-100% of setpoint range) |  | 0.01 | % |  | x | x | x | x | x | x | x | x | x
00339 | [R] | MeasuredData.DiffPressure | Differential pump pressure |  | 0.001 | bar | [5 empty] | xs |  |  | x
00340 | [R] | MeasuredData.OutletPressure | Outlet pressure |  | 0.001 | bar | [5 empty] | xs
00341 | [R] | MeasuredData.RemotePressure2 | Remote pressure 2 |  | 0.001 | bar | [5 empty] | xs
00342 | [R] | MeasuredData.LoadPercent | Motor current in pct. Of nominal motor current |  | 0.01 | % | [5 empty] | x
00343 | [R] | MeasuredData.PumpUnixRtc_HI | Pump time and date in UNIX format |  | 1 | s | [5 empty] | x |  |  | x
00344 | [R] | MeasuredData.PumpUnixRtc_LO | [9 empty] | x |  |  | x
00345 | [R] | MeasuredData.MaxFlowLimit | Actual maximum flow limit |  | 0.01 | m3/h | [5 empty] | x |  |  | x
00346 | [R] | MeasuredData.RemoteDiffTemp | Remote differential temperature |  | 0.01 | K | [5 empty] | xs
00347 | [R] | MeasuredData.InletDiffPressure | Inlet differential pressure |  | 0.001 | bar | [5 empty] | xs
00348 | [R] | MeasuredData.OutletDiffPressure | Outlet differential pressure |  | 0.001 | bar | [5 empty] | xs
00349 | [R] | MeasuredData.RemoteDiffPressure | Remote differential pressure |  | 0.001 | bar | [5 empty] | xs
00350 | [R] | MeasuredData.StorageTankLevel | Storage tank level |  | 0.01 | m | [5 empty] | xs
00351 | [R] | MeasuredData.AmbientTemp | Ambient temperature |  | 0.01 | K | [5 empty] | xs
00352 | [R] | MeasuredData.HeatEnergyCounter1_HI | Accumulated heat energy in total pump life time (direction 1) |  | 1 | kWh | [5 empty] | xs |  |  | xs
00353 | [R] | MeasuredData.HeatEnergyCounter1_LO | [9 empty] | xs |  |  | xs
00354 | [R] | MeasuredData.HeatPower_HI | Current heat power |  | 1 | W | [5 empty] | xs |  |  | xs
00355 | [R] | MeasuredData.HeatPower_LO | [9 empty] | xs |  |  | xs
00356 | [R] | MeasuredData.HeatDiffTemp | Differential temperature between forward and return pipes |  | 0.01 | C | [5 empty] | xs |  |  | xs
00357 | [R] | MeasuredData.Volume1 HI | Pumped volume in total pump life time (direction 1) |  | 0.01 | m³ | [5 empty] | xs | x |  | x
00358 | [R] | MeasuredData.Volume1 LO | [9 empty] | xs | x |  | x
00359 | [R] | MeasuredData.HeatEnergyCounter2_HI | Accumulated heat energy in total pump life time (direction 2) |  | 1 | kWh | [5 empty] | xs |  |  | xs
00360 | [R] | MeasuredData.HeatEnergyCounter2_LO | [9 empty] | xs |  |  | xs
00361 | [R] | MeasuredData.Volume2 HI | Pumped volume total pump life time (direction 2) |  | 0.01 | m³ | [5 empty] | xs |  |  | x
00362 | [R] | MeasuredData.Volume2 LO | [9 empty] | xs |  |  | x
00363 | [R] | MeasuredData.Conductivity | Conductivity measurement |  | 0.1 | NTU | [5 empty] | xs
00364 | [R] | MeasuredData.PHMeasure | PH measurement |  | 0.01 | PH | [5 empty] | xs
00365 | [R] | MeasuredData.Turbidity | Turbidity measurement |  | 1 | uS/cm | [5 empty] | xs
SIMULATION [R/W]
00701 | [W] | Simulation.AlarmCode | Write a supported alarm code |  |  | enum |  |  |  | x | x | x |  | x | x
00702 | [W] | Simulation.WarningCode | Write a supported warning code |  |  | enum |  |  |  | x | x | x |  |  | x
00703 | [W] | Simulation.EventCode |  |  |  | enum
00704 | [W] | Simulation.DeviceType |  |  |  | enum
00705 | [W] | Simulation.DeviceNumber |  |  |  | enum
00706 | [W] | Simulation.ActionType |  |  |  | enum
00707 | [W] | Simulation.ResetType |  |  |  | enum
00708 | [W] | Simulation.Activate | Must be Remote controlled | 0 = Deactivate 1 = Activate |  | bool |  |  |  | x x | x x | x x |  | x x | x x
00709 | [R] | Simulation.Active |  |  |  | bool |  |  |  | x | x | x |  | x | x
USER REGISTERS [R/W]
00751 | [R/W] | UserLabel1 |  |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00752 | [R/W] | UserLabel2 |  |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00753 | [R/W] | UserLabel3 |  |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00754-00799 | [R/W] | UserLabel4-UserLabel49 |  |  |  | unscaled |  | x | x | x | x | x | x | x | x | x
00800 | [R/W] | UserLabel50 |  |  |  | unscaled |  | x | x | x | x | x | x | x | x | x

## CIM 550 P
GRUNDFOS CIM 550 P SYSPro extended MODBUS profile for pumps
All addresses are registers (16 bit), and the address is written in decimal format.
Sheet version: 01.00.00
Change date (d-m-y): 16-05-2025
Reg. addr. | Access | Modbus parameter name | Description | Bool/Enum description | Modbus Scale | Modbus Unit | Modbus Offset | HM2000 | HM3000 | HM3000 Midlife | HM Large | MGE H/I/J/K | CUE | Magna | MAGNA3 | LaUPE / DAB
Setting CIM 550 P SYSPro parameters
00131 | [W] | SetMinFrequency | Selection of min pump frequency in % of nominal frequency |  | 0.01 | % | [5 empty] | x
00132 | [W] | SetMaxFrequency | Selection of max pump frequency in % of nominal frequency |  | 0.01 | % | [5 empty] | x
00133 | [W] | SetAnaIn1Unit | Selection of scaling unit for AI1 measurement | 0 = bar 1 = mbar 2 = m 3 = kPa 4 = psi 5 = feet 6 = m3/h 7 = m3/s 8 = ltr/s 9 = gal/min (GPM) 10 = celsius 11 = farenheit 12 = % 21 = in 22 = yd3/h |  | enum | [5 empty] | x
00134 | [W] | SetAnaIn1Min | Selection of minimum value for AI1 measurement |  |  | unscaled | [5 empty] | x
00135 | [W] | SetAnaIn1Max | Selection of maximum value for AI1 measurement |  |  | unscaled | [5 empty] | x
00136 | [W] | SetAnaIn1SigType | Selection of signal type for AI1 measurement | 0 = 0-20 mA 1 = 0-5 V 2 = 0-10 V 3 = 4-20 mA 4 = - 5 = 0.5-3.5 V |  | enum | [5 empty] | x
00137 | [W] | SetAnaIn1Applic | Selection of application for AI1 measurement | 0 = Inlet pressure 1 = Inlet diff. pressure 2 = Outlet pressure 3 = Outlet diff. pressure 4 = Pump diff. pressure 5 = Remote pressure 1 6 = Remote pressure 2 7 = Remote diff. pressure 8 = Feed tank pressure/level 9 = Storage tank pressure/level 40 = Pump flow 41 = Remote flow 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00138 | [W] | SetAnaIn1Func | Selection of function for AI1 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00139 | [W] | SetAnaIn2Unit | Selection of scaling unit for AI2 measurement | 0 = bar 1 = mbar 2 = m 3 = kPa 4 = psi 5 = feet 6 = m3/h 7 = m3/s 8 = ltr/s 9 = gal/min (GPM) 10 = celsius 11 = farenheit 12 = % 21 = in 22 = yd3/h |  | enum | [5 empty] | x
00140 | [W] | SetAnaIn2Min | Selection of minimum value for AI2 measurement |  |  | unscaled | [5 empty] | x
00141 | [W] | SetAnaIn2Max | Selection of maximum value for AI2 measurement |  |  | unscaled | [5 empty] | x
00142 | [W] | SetAnaIn2SigType | Selection of signal type for AI2 measurement | 0 = 0-20 mA 1 = 0-5 V 2 = 0-10 V 3 = 4-20 mA 4 = - 5 = 0.5-3.5 V |  | enum | [5 empty] | x
00143 | [W] | SetAnaIn2Applic | Selection of application for AI1 measurement | 0 = Inlet pressure 1 = Inlet diff. pressure 2 = Outlet pressure 3 = Outlet diff. pressure 4 = Pump diff. pressure 5 = Remote pressure 1 6 = Remote pressure 2 7 = Remote diff. pressure 8 = Feed tank pressure/level 9 = Storage tank pressure/level 40 = Pump flow 41 = Remote flow 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00144 | [W] | SetAnaIn2Func | Selection of function for AI2 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00145 | [W] | SetAnaIn3Unit | Selection of scaling unit for AI3 measurement | 0 = bar 1 = mbar 2 = m 3 = kPa 4 = psi 5 = feet 6 = m3/h 7 = m3/s 8 = ltr/s 9 = gal/min (GPM) 10 = celsius 11 = farenheit 12 = % 21 = in 22 = yd3/h |  | enum | [5 empty] | x
00146 | [W] | SetAnaIn3Min | Selection of minimum value for AI3 measurement |  |  | unscaled | [5 empty] | x
00147 | [W] | SetAnaIn3Max | Selection of maximum value for AI3 measurement |  |  | unscaled | [5 empty] | x
00148 | [W] | SetAnaIn3SigType | Selection of signal type for AI3 measurement | 0 = 0-20 mA 1 = 0-5 V 2 = 0-10 V 3 = 4-20 mA 4 = - 5 = 0.5-3.5 V |  | enum | [5 empty] | x
00149 | [W] | SetAnaIn3Applic | Selection of application for AI3 measurement | 0 = Inlet pressure 1 = Inlet diff. pressure 2 = Outlet pressure 3 = Outlet diff. pressure 4 = Pump diff. pressure 5 = Remote pressure 1 6 = Remote pressure 2 7 = Remote diff. pressure 8 = Feed tank pressure/level 9 = Storage tank pressure/level 40 = Pump flow 41 = Remote flow 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00150 | [W] | SetAnaIn3Func | Selection of function for AI3 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00151 | [W] | SetTempIn1Applic | Selection of application for T1 measurement | 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00152 | [W] | SetTempIn1Func | Selection of function for T1 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00153 | [W] | SetTempIn2Applic | Selection of application for T2 measurement | 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00154 | [W] | SetTempIn2Func | Selection of function for T2 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00155 | [W] | SetLiqTecTempFunc | Selection of function for LiqTec temperature measurement, LT | 0 = Not active 1 = Control loop feedback 2= Reference influence (no function) 3 = Other measurement |  | enum | [5 empty] | x
00156 | [W] | SetGrfSensorPressFunc | Selection of function for Grundfos sensor press. Measurement, GP | 0 = Not active 1 = Control loop feedback 2= Reference influence (no function) 3 = Other measurement |  | enum | [5 empty] | x
00157 | [W] | SetGrfSensorTempFunc | Selection of function for Grundfos sensor temp. measurement, GT | 0 = Not active 1 = Control loop feedback (no function) 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00158 | [W] | SetDigInPolarity | Selection of polarity for DI1-4 by bit 0-3, 0=active closed |  |  | bits | [5 empty] | x
00159 | [W] | SetDigIODirection | Selection of In/Out direction for DI3/DO3 and DI4/DO4 | 0 = DI3 and DI4 1 = DO3 and DI4 2 = DI3 and DO4 3 = DO3 and DO4 |  | enum | [5 empty] | x
00160 | [W] | SetDigIn1Func | Selection of DI1 function | 0 = Operating mode "Min" 1 = Operating mode "Max" 2 = Operating mode " Stop" 3 = Reverse direction 4 = Alarm reset 5 = External fault 6 = External flow switch 10 = Dry running detection 11 = Water from mains 12 = Pulse counter 13 = Predefinet setpoint digit 1 14 = Predefinet setpoint digit 2 52 = Predefinet setpoint digit 3 53 = Operating mode "UserCurve" 54 = Local stop of pump (Multi-E) 253 = DI1 --> DO1 254 = Not active |  | enum | [5 empty] | x
00161 | [W] | SetDigIn2Func | Selection of DI2 function | 0 = Operating mode "Min" 1 = Operating mode "Max" 2 = Operating mode " Stop" 3 = Reverse direction 4 = Alarm reset 5 = External fault 6 = External flow switch 10 = Dry running detection 11 = Water from mains 12 = Pulse counter 13 = Predefinet setpoint digit 1 14 = Predefinet setpoint digit 2 52 = Predefinet setpoint digit 3 53 = Operating mode "UserCurve" 54 = Local stop of pump (Multi-E) 253 = DI1 --> DO1 254 = Not active |  | enum | [5 empty] | x
00162 | [W] | SetDigIn3Func | Selection of DI3 function | 0 = Operating mode "Min" 1 = Operating mode "Max" 2 = Operating mode " Stop" 3 = Reverse direction 4 = Alarm reset 5 = External fault 6 = External flow switch 10 = Dry running detection 11 = Water from mains 12 = Pulse counter 13 = Predefinet setpoint digit 1 14 = Predefinet setpoint digit 2 52 = Predefinet setpoint digit 3 53 = Operating mode "UserCurve" 54 = Local stop of pump (Multi-E) 253 = DI1 --> DO1 254 = Not active |  | enum | [5 empty] | x
00163 | [W] | SetDigIn4Func | Selection of DI4 function | 0 = Operating mode "Min" 1 = Operating mode "Max" 2 = Operating mode " Stop" 3 = Reverse direction 4 = Alarm reset 5 = External fault 6 = External flow switch 10 = Dry running detection 11 = Water from mains 12 = Pulse counter 13 = Predefinet setpoint digit 1 14 = Predefinet setpoint digit 2 52 = Predefinet setpoint digit 3 53 = Operating mode "UserCurve" 54 = Local stop of pump (Multi-E) 253 = DI1 --> DO1 254 = Not active |  | enum | [5 empty] | x
00164 | [W] | SetDigOut1Func | Selection of DO1 function | 0 = Not active 1 = Running 2 = Service warning, time to lubricate 3 = Limit 1 exceeded 4 = Limit 2 exeeded 5 = Warning 6 = Alarm, active or unacknowledged 7 = Alarm, active 8 = Operating 9 = Ready 10 = Bus controlled 11 = External fan control 12 = Pump at limit 13 = Changed to mains water 14 = Multi-E, at least one pump running 15 = Multi-E, all pumps have active alarms 16 = Multi-E, at least one pump has alarm 17 = Multi-E, at least one pump is ready 18 = DI1 status 19 = DI2 status 20 = DI3 status 21 = DI4 status |  | enum | [5 empty] | x
00165 | [W] | SetDigOut2Func | Selection of DO2 function | 0 = Not active 1 = Running 2 = Service warning, time to lubricate 3 = Limit 1 exceeded 4 = Limit 2 exeeded 5 = Warning 6 = Alarm, active or unacknowledged 7 = Alarm, active 8 = Operating 9 = Ready 10 = Bus controlled 11 = External fan control 12 = Pump at limit 13 = Changed to mains water 14 = Multi-E, at least one pump running 15 = Multi-E, all pumps have active alarms 16 = Multi-E, at least one pump has alarm 17 = Multi-E, at least one pump is ready 18 = DI1 status 19 = DI2 status 20 = DI3 status 21 = DI4 status |  | enum | [5 empty] | x
00166 | [W] | SetDigOut3Func | Selection of DO3 function | 0 = Not active 1 = Running 2 = Service warning, time to lubricate 3 = Limit 1 exceeded 4 = Limit 2 exeeded 5 = Warning 6 = Alarm, active or unacknowledged 7 = Alarm, active 8 = Operating 9 = Ready 10 = Bus controlled 11 = External fan control 12 = Pump at limit 13 = Changed to mains water 14 = Multi-E, at least one pump running 15 = Multi-E, all pumps have active alarms 16 = Multi-E, at least one pump has alarm 17 = Multi-E, at least one pump is ready 18 = DI1 status 19 = DI2 status 20 = DI3 status 21 = DI4 status |  | enum | [5 empty] | x
00167 | [W] | SetDigOut4Func | Selection of DO4 function | 0 = Not active 1 = Running 2 = Service warning, time to lubricate 3 = Limit 1 exceeded 4 = Limit 2 exeeded 5 = Warning 6 = Alarm, active or unacknowledged 7 = Alarm, active 8 = Operating 9 = Ready 10 = Bus controlled 11 = External fan control 12 = Pump at limit 13 = Changed to mains water 14 = Multi-E, at least one pump running 15 = Multi-E, all pumps have active alarms 16 = Multi-E, at least one pump has alarm 17 = Multi-E, at least one pump is ready 18 = DI1 status 19 = DI2 status 20 = DI3 status 21 = DI4 status |  | enum | [5 empty] | x
00168 | [W] | SetAnaOutSigType | Selection of AO signal type | 0 = 0-20 mA 1 = - 2 = 0-10 V 3 = 4-20 mA 4 = - 5 = - |  | enum | [5 empty] | x
00169 | [W] | SetAnaOutParm | Selection of AO output parameter | 0 = Motor speed, 0-200% 1 = Feedback sensor value 2 = Control loop reference 3 = Motor load, 0-200% 4 = Motor current, 0-200% 5 = Limit 1 exceeded [bool] 6 = Limit 2 exceeded [bool] 7 = Pump flow, 0-200% |  | enum | [5 empty] | x
Status of CIM 550 P SYSPro parameters
00250 | [R] | StatusAnaIn1Unit | Status of scaling unit for AI1 measurement | 0 = bar 1 = mbar 2 = m 3 = kPa 4 = psi 5 = feet 6 = m3/h 7 = m3/s 8 = ltr/s 9 = gal/min (GPM) 10 = celsius 11 = farenheit 12 = % 21 = in 22 = yd3/h |  | enum | [5 empty] | x
00251 | [R] | StatusAnaIn1Min | Status of minimum value for AI1 measurement |  |  | unscaled | [5 empty] | x
00252 | [R] | StatusAnaIn1Max | Status of maximum value for AI1 measurement |  |  | unscaled | [5 empty] | x
00253 | [R] | StatusAnaIn1SigType | Status of signal type for AI1 measurement | 0 = 0-20 mA 1 = 0-5 V 2 = 0-10 V 3 = 4-20 mA 4 = - 5 = 0.5-3.5 V |  | enum | [5 empty] | x
00254 | [R] | StatusAnaIn1Applic | Status of application for AI1 measurement | 0 = Inlet pressure 1 = Inlet diff. pressure 2 = Outlet pressure 3 = Outlet diff. pressure 4 = Pump diff. pressure 5 = Remote pressure 1 6 = Remote pressure 2 7 = Remote diff. pressure 8 = Feed tank pressure/level 9 = Storage tank pressure/level 40 = Pump flow 41 = Remote flow 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00255 | [R] | StatusAnaIn1Func | Status of function for AI1 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00256 | [R] | Status.AnaIn2Unit | Status of scaling unit for AI2 measurement | 0 = bar 1 = mbar 2 = m 3 = kPa 4 = psi 5 = feet 6 = m3/h 7 = m3/s 8 = ltr/s 9 = gal/min (GPM) 10 = celsius 11 = farenheit 12 = % 21 = in 22 = yd3/h |  | enum | [5 empty] | x
00257 | [R] | Status.AnaIn2Min | Status of minimum value for AI2 measurement |  |  | unscaled | [5 empty] | x
00258 | [R] | Status.AnaIn2Max | Status of maximum value for AI2 measurement |  |  | unscaled | [5 empty] | x
00259 | [R] | Status.AnaIn2SigType | Status of signal type for AI2 measurement | 0 = 0-20 mA 1 = 0-5 V 2 = 0-10 V 3 = 4-20 mA 4 = - 5 = 0.5-3.5 V |  | enum | [5 empty] | x
00260 | [R] | Status.AnaIn2Applic | Status of application for AI1 measurement | 0 = Inlet pressure 1 = Inlet diff. pressure 2 = Outlet pressure 3 = Outlet diff. pressure 4 = Pump diff. pressure 5 = Remote pressure 1 6 = Remote pressure 2 7 = Remote diff. pressure 8 = Feed tank pressure/level 9 = Storage tank pressure/level 40 = Pump flow 41 = Remote flow 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00261 | [R] | Status.AnaIn2Func | Status of function for AI2 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00262 | [R] | Status.AnaIn3Unit | Status of scaling unit for AI3 measurement | 0 = bar 1 = mbar 2 = m 3 = kPa 4 = psi 5 = feet 6 = m3/h 7 = m3/s 8 = ltr/s 9 = gal/min (GPM) 10 = celsius 11 = farenheit 12 = % 21 = in 22 = yd3/h |  | enum | [5 empty] | x
00263 | [R] | Status.AnaIn3Min | Status of minimum value for AI3 measurement |  |  | unscaled | [5 empty] | x
00264 | [R] | Status.AnaIn3Max | Status of maximum value for AI3 measurement |  |  | unscaled | [5 empty] | x
00265 | [R] | Status.AnaIn3SigType | Status of signal type for AI3 measurement | 0 = 0-20 mA 1 = 0-5 V 2 = 0-10 V 3 = 4-20 mA 4 = - 5 = 0.5-3.5 V |  | enum | [5 empty] | x
00266 | [R] | Status.AnaIn3Applic | Status of application for AI3 measurement | 0 = Inlet pressure 1 = Inlet diff. pressure 2 = Outlet pressure 3 = Outlet diff. pressure 4 = Pump diff. pressure 5 = Remote pressure 1 6 = Remote pressure 2 7 = Remote diff. pressure 8 = Feed tank pressure/level 9 = Storage tank pressure/level 40 = Pump flow 41 = Remote flow 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00267 | [R] | Status.AnaIn3Func | Status of function for AI3 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00268 | [R] | Status.TempIn1Applic | Status of application for T1 measurement | 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00269 | [R] | Status.TempIn1Func | Status of function for T1 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00270 | [R] | Status.TempIn2Applic | Status of application for T2 measurement | 80 = Medium temperature 81 = Forward temperature 82 = Return temperature 83 = Remote diff. temperature 84 = Remote medium temp. 1 85 = Remote medium temp. 2 88 = Ambient temp. (room) 89 = Ambient temp. (outdoor) 90 = Motor winding temp. 91 = Motor bearing drive-end temp. 92 = Motor bearing non-drive-end temp 120 = Other. |  | enum | [5 empty] | x
00271 | [R] | Status.TempIn2Func | Status of function for T2 measurement | 0 = Not active 1 = Control loop feedback 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00272 | [R] | Status.LiqTecTempFunc | Status of function for LiqTec temperature measurement, LT | 0 = Not active 1 = Control loop feedback 2= Reference influence (no function) 3 = Other measurement |  | enum | [5 empty] | x
00273 | [R] | Status.GrfSensorPressFunc | Status of function for Grundfos sensor press. Measurement, GP | 0 = Not active 1 = Control loop feedback 2= Reference influence (no function) 3 = Other measurement |  | enum | [5 empty] | x
00274 | [R] | Status.GrfSensorTempFunc | Status of function for Grundfos sensor temp. measurement, GT | 0 = Not active 1 = Control loop feedback (no function) 2= Reference influence 3 = Other measurement |  | enum | [5 empty] | x
00275 | [R] | Status.DigInPolarity | Status of polarity for DI1-4 by bit 0-3, 0=active closed |  |  | bits | [5 empty] | x
00276 | [R] | Status.DigIODirection | Status of In/Out direction for DI3/DO3 and DI4/DO4 | 0 = DI3 and DI4 1 = DO3 and DI4 2 = DI3 and DO4 3 = DO3 and DO4 |  | enum | [5 empty] | x
00277 | [R] | Status.DigIn1Func | Status of DI1 function | 0 = Operating mode "Min" 1 = Operating mode "Max" 2 = Operating mode " Stop" 3 = Reverse direction 4 = Alarm reset 5 = External fault 6 = External flow switch 10 = Dry running detection 11 = Water from mains 12 = Pulse counter 13 = Predefinet setpoint digit 1 14 = Predefinet setpoint digit 2 52 = Predefinet setpoint digit 3 53 = Operating mode "UserCurve" 54 = Local stop of pump (Multi-E) 253 = DI1 --> DO1 254 = Not active |  | enum | [5 empty] | x
00278 | [R] | Status.DigIn2Func | Status of DI2 function | 0 = Operating mode "Min" 1 = Operating mode "Max" 2 = Operating mode " Stop" 3 = Reverse direction 4 = Alarm reset 5 = External fault 6 = External flow switch 10 = Dry running detection 11 = Water from mains 12 = Pulse counter 13 = Predefinet setpoint digit 1 14 = Predefinet setpoint digit 2 52 = Predefinet setpoint digit 3 53 = Operating mode "UserCurve" 54 = Local stop of pump (Multi-E) 253 = DI1 --> DO1 254 = Not active |  | enum | [5 empty] | x
00279 | [R] | Status.DigIn3Func | Status of DI3 function | 0 = Operating mode "Min" 1 = Operating mode "Max" 2 = Operating mode " Stop" 3 = Reverse direction 4 = Alarm reset 5 = External fault 6 = External flow switch 10 = Dry running detection 11 = Water from mains 12 = Pulse counter 13 = Predefinet setpoint digit 1 14 = Predefinet setpoint digit 2 52 = Predefinet setpoint digit 3 53 = Operating mode "UserCurve" 54 = Local stop of pump (Multi-E) 253 = DI1 --> DO1 254 = Not active |  | enum | [5 empty] | x
00280 | [R] | Status.DigIn4Func | Status of DI4 function | 0 = Operating mode "Min" 1 = Operating mode "Max" 2 = Operating mode " Stop" 3 = Reverse direction 4 = Alarm reset 5 = External fault 6 = External flow switch 10 = Dry running detection 11 = Water from mains 12 = Pulse counter 13 = Predefinet setpoint digit 1 14 = Predefinet setpoint digit 2 52 = Predefinet setpoint digit 3 53 = Operating mode "UserCurve" 54 = Local stop of pump (Multi-E) 253 = DI1 --> DO1 254 = Not active |  | enum | [5 empty] | x
00281 | [R] | Status.DigOut1Func | Status of DO1 function | 0 = Not active 1 = Running 2 = Service warning, time to lubricate 3 = Limit 1 exceeded 4 = Limit 2 exeeded 5 = Warning 6 = Alarm, active or unacknowledged 7 = Alarm, active 8 = Operating 9 = Ready 10 = Bus controlled 11 = External fan control 12 = Pump at limit 13 = Changed to mains water 14 = Multi-E, at least one pump running 15 = Multi-E, all pumps have active alarms 16 = Multi-E, at least one pump has alarm 17 = Multi-E, at least one pump is ready 18 = DI1 status 19 = DI2 status 20 = DI3 status 21 = DI4 status |  | enum | [5 empty] | x
00282 | [R] | Status.DigOut2Func | Status of DO2 function | 0 = Not active 1 = Running 2 = Service warning, time to lubricate 3 = Limit 1 exceeded 4 = Limit 2 exeeded 5 = Warning 6 = Alarm, active or unacknowledged 7 = Alarm, active 8 = Operating 9 = Ready 10 = Bus controlled 11 = External fan control 12 = Pump at limit 13 = Changed to mains water 14 = Multi-E, at least one pump running 15 = Multi-E, all pumps have active alarms 16 = Multi-E, at least one pump has alarm 17 = Multi-E, at least one pump is ready 18 = DI1 status 19 = DI2 status 20 = DI3 status 21 = DI4 status |  | enum | [5 empty] | x
00283 | [R] | Status.DigOut3Func | Status of DO3 function | 0 = Not active 1 = Running 2 = Service warning, time to lubricate 3 = Limit 1 exceeded 4 = Limit 2 exeeded 5 = Warning 6 = Alarm, active or unacknowledged 7 = Alarm, active 8 = Operating 9 = Ready 10 = Bus controlled 11 = External fan control 12 = Pump at limit 13 = Changed to mains water 14 = Multi-E, at least one pump running 15 = Multi-E, all pumps have active alarms 16 = Multi-E, at least one pump has alarm 17 = Multi-E, at least one pump is ready 18 = DI1 status 19 = DI2 status 20 = DI3 status 21 = DI4 status |  | enum | [5 empty] | x
00284 | [R] | Status.DigOut4Func | Status of DO4 function | 0 = Not active 1 = Running 2 = Service warning, time to lubricate 3 = Limit 1 exceeded 4 = Limit 2 exeeded 5 = Warning 6 = Alarm, active or unacknowledged 7 = Alarm, active 8 = Operating 9 = Ready 10 = Bus controlled 11 = External fan control 12 = Pump at limit 13 = Changed to mains water 14 = Multi-E, at least one pump running 15 = Multi-E, all pumps have active alarms 16 = Multi-E, at least one pump has alarm 17 = Multi-E, at least one pump is ready 18 = DI1 status 19 = DI2 status 20 = DI3 status 21 = DI4 status |  | enum | [5 empty] | x
00285 | [R] | Status.AnaOutSigType | Status of AO signal type | 0 = 0-20 mA 1 = - 2 = 0-10 V 3 = 4-20 mA 4 = - 5 = - |  | enum | [5 empty] | x
00286 | [R] | Status.AnaOutParm | Status of AO output parameter | 0 = Motor speed, 0-200% 1 = Feedback sensor value 2 = Control loop reference 3 = Motor load, 0-200% 4 = Motor current, 0-200% 5 = Limit 1 exceeded [bool] 6 = Limit 2 exceeded [bool] 7 = Pump flow, 0-200% |  | enum | [5 empty] | x
Sensor measurements CIM 550 P SYSPro
00370 | [R] | MeasuredData.AnalogIn1 | Direct reading of Analog Input 1 (AI1) measurement |  | 0.01 | % | [5 empty] | xs
00371 | [R] | MeasuredData.AnalogIn2 | Direct reading of Analog Input 2 (AI2) measurement |  | 0.01 | % | [5 empty] | xs
00372 | [R] | MeasuredData.AnalogIn3 | Direct reading of Analog Input 2 (AI3) measurement |  | 0.01 | % | [5 empty] | xs
00373 | [R] | MeasuredData.GrfSensorPress | Direct reading of Grundfos pressure sensor (GP) measurement |  | 0.01 | % | [5 empty] | xs
00374 | [R] | MeasuredData.GrfSensorTemp | Direct reading of Grundfos temperature sensor (GT) measurement |  | 0.01 | % | [5 empty] | xs
00375 | [R] | MeasuredData.TempIn1 | Direct reading of temperature sensor 1 (T1) measurement |  | 0.01 | K | [5 empty] | xs
00376 | [R] | MeasuredData.TempIn2 | Direct reading of temperature sensor 2 (T2) measurement |  | 0.01 | K | [5 empty] | xs
00377 | [R] | MeasuredData.LiqTecTemp | Direct reading of LiqTec temperature sensor (LT) measurement |  | 0.01 | K | [5 empty] | xs

## Booster
GRUNDFOS CIM 200/260/500 MODBUS profile for boosters
All addresses are registers (16 bit), and the address is written in decimal format.
Sheet version: 02.10.03
Change date (d-m-y): 16-05-2025
Reg. addr. | Access | Modbus parameter name | Description | Bool/Enum description | Modbus Scale | Modbus Unit | Modbus Offset | MPC CU 352 | Multi-B CU 323 | Multi-E F/G | Redwolf Multi | DDD CU 354 | Multi-E H/I/J/K | MAGNA3-D
DEVICE CONFIG [R/W] - All saved in EEPROM
00001 | [R/W] | Config.SlaveMinimumReplyDelay | For adding a reply delay in ms (used with radio modem) |  | 1 | ms |  | x | x | x | x | X | x | x
00002 | [R/W] | RESERVED
00003 | [R/W] | Config.SoftwareDefinedModbusAddress | Set a Modbus slave address to use if the address switches are set to an invalid value (Modbus RTU only). |  |  | unscaled |  | x | x | x | x | X | x | x
00004 | [R/W] | Config.ModbusBitRate | If set to software defined, use this bit rate (Modbus RTU only). | 0 = 1200 1 = 2400 2 = 4800 3 = 9600 4 = 19200 5 = 38400 |  | enum |  | x | x | x | x | X | x | x
00005 | [R/W] | Config.AutoAckControlBits | Acknowlege behaviour of control bits | 0 = Manual, 1 = Automatic |  | bool |  | x | x | x | x | X | x | x
00006 |  | RESERVED
00007 | [R/W] | Config.ScadaCallbackRegister | Register in the master used for unsolicited messages. (GSM/GRPS only) |  |  | unscaled
00008 | [R/W] | Config.NoDataActivityTimeout | The elapsed time with no data activity before the module issues a "GPRS restart". (GSM/GRPS only) |  | 1 | min
00009 | [R/W] | Config.SoftwareDefinedParity | If software defined, use this parity setting (Modbus RTU only). | 0 = No parity 1 = Even parity 2 = Odd parity |  | enum |  | x | x | x | x | X | x | x
00010 | [R/W] | Config.SoftwareDefinedStopBit | If software defined, use this stop bit setting (Modbus RTU only) | 0 = Not defined 1 = 1 stop bit 2 = 2 stop bit |  | enum |  | x | x | x | x | X | x | x
00011 | [R/W] | Config.ScadaPinCode | Code to use if ScadaPinCode is enabled (GSM/GPRS only) |  |  |  |  | x | x | x | x | X | x | x
00012 | [R/W] | Config.Watchdog | Saved in EEPROM. Default = 0 (Disabled). Values 1-4 will set value=5. Values >3600 will set value=3600. Watchdog sets pump in Local mode Only for CIM 200 and CIM 500 |  | 1 | s |  | x | x | x | x | X | x | x
00013 | [R/W] | Config.GENIbusDiodeOff | Switching off the GENIbus diode (LED2) | 0=On (default) 1=Off |  | bool |  | x | x | x | x | X | x | x
DEVICE STATUS [R]
00021 | [R] | GENIbusCRCErrorCnt | CRC error counter on GENIbus |  |  | unscaled |  | x | x | x | x | x | x | x
00022 | [R] | GENIbusDataErrorCnt | Data error counter on GENIbus |  |  | unscaled |  | x | x | x | x | x | x | x
00023 | [R] | VersionNumber | CIM software version number |  |  | unscaled |  | x | x | x | x | x | x | x
00024 | [R] | ActualModbusAddress | Actual modbus slave address (Read only) |  |  | unscaled |  | x | x | x | x | x | x | x
00025 | [R] | GENIbusTXcount HI | Transmit counter on GENIbus |  |  | unscaled |  | x | x | x | x | x | x | x
00026 | [R] | GENIbusTXcount LO | [5 empty] | x | x | x | x | x | x | x
00027 | [R] | GENIbusRXcount HI | Receive counter on GENIbus |  |  | unscaled |  | x | x | x | x | x | x | x
00028 | [R] | GENIbusRXcount LO | [5 empty] | x | x | x | x | x | x | x
00029.0 | [R] | ScadaPinCodeEnabled | Determines if the use of a Scada Pin Code is enabled (GSM/GPRS only) | 0 = Pin code disabled 1 = Pin code enabled |  |  |  | x | x | x | x | x | x | x
00029.1 | [R] | WriteAccessStatus | Determines if write (control) access is granted or not (GSM/GPRS only) | 0 = No write access 1 = Write access
00029.2 | [R] | LockinBlocked | Login blocked due to too many password attempts | 0 = No Login blocking 1 = Login blocked
00030 | [R] | GrundfosUnitFamily | Grundfos product family | 0 = - 1 = MAGNA series 2 = MGE series 7 = Motor Protection Unit 17 = Multi-E booster 21 = MPC / Multi-B 25 = CR Monitor 26 = Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller CU 2X1 48 = Level controller LC 2x1 65 = SQ Controller CU 202/302 255 = N/A |  | enum |  | x | x | x | x | x | x | x
00031 | [R] | GrundfosUnitType | Grundfos product type number |  |  | unscaled |  | x | x | x | x | x | x | x
00032 | [R] | GrundfosUnitVersion | Grundfos product version number |  |  | unscaled |  | x | x | x | x | x | x | x
00033 | [R] | BatteryState | State of cellular module battery | 0 = Battery not present 1 = Battery must be replaced 2 = Battery charging 3 = Battery needs charging, but temperature too high 4 = Battery needs charging, but temperature too low 5 = Battery Low 6 = Battery OK 255 = Battery state not available |  | enum |  | x | x | x | x | x | x | x
00034 | [R] | ProductSoftwareVersionHI | Product software version (BCD digit 1-4 aa.bb) |  |  | BCD number |  | x |  |  |  | x
00035 | [R] | ProductSoftwareVersionLO | Product software version (BCD digit 5-8 cc.dd) |  |  | BCD number |  | x |  |  |  | x
00036 | [R] | ProductSoftwareDayMonth | Product software date (BCD ddmm) |  |  | BCD number |  | x |  |  |  | x
00037 | [R] | ProductSoftwareYear | Product software date (BCD yyyy) |  |  | BCD number |  | x |  |  |  | x
GSM REAL TIME CLOCK [R/W] (ONLY AVAILABLE IN CIM 25X!)
00080 | [W] | SetUNIXRealTimeClockHI | Set Real Time Clock (32 bit UNIX format) (GSM/GPRS only) |  | 1 | s |  | x | x | x | x | x | x | x
00081 | [W] | SetUNIXRealTimeClockLO | [5 empty] | x | x | x | x | x | x | x
00082 | [W] | SetRtcSecond | Set Real Time Clock (Seconds) (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00083 | [W] | SetRtcMinute | Set Real Time Clock (Minutes) (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00084 | [W] | SetRtcHour | Set Real Time Clock (Hours) (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00085 | [W] | SetRtcDay | Set Real Time Clock (Day) (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00086 | [W] | SetRtcMonth | Set Real Time Clock (Month) (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00087 | [W] | SetRtcYear | Set Real Time Clock (Year - after 2000) (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00088.0 | [W] | SetRtc | Set Real Time Clock (Normal format) (GSM/GPRS only) | 0 = No command 1 = Set the clock |  | bool |  | x | x | x | x | x | x | x
00089 | [R] | Status.UNIXRealTimeClockHI | Real Time Clock (32 bit UNIX format) (GSM/GPRS only) |  | 1 | s |  | x | x | x | x | x | x | x
00090 | [R] | Status.UNIXRealTimeClockLO | [5 empty] | x | x | x | x | x | x | x
00091 | [R] | Status.RtcSecond | Real time clock - Seconds (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00092 | [R] | Status.RtcMinute | Real time clock - Minutes (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00093 | [R] | Status.RtcHour | Real time clock - Hours (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00094 | [R] | Status.RtcDay | Real time clock - Day of month (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00095 | [R] | Status.RtcMonth | Real time clock - Month (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00096 | [R] | Status.RtcYear | Real time clock - Year (after 2000) (GSM/GPRS only) |  |  | enum |  | x | x | x | x | x | x | x
00097.0 | [R] | Status.AcknowledgeSetRTC | Acknowledge of Set Real Time Clock command (GSM/GPRS only) | 0 = No acknowledge 1 = Acknowledged |  | bool |  | x | x | x | x | x | x | x
CONTROL [W]
00101.5 | [W] | Control.ResetAccCounters |  | 0 = No resetting 1 = Reset counters |  | bool |  | x | - | - | - | x | x | -
00101.4 | [W] | Control.CopyToLocal | Copies Operating mode, Control mode and Setpoint to Local, when changing from Remote to Local (Multi-E type H/I only) | 0 = Do not copy 1 = Copy to local |  | bool |  | - | - | - |  | - | x | x
00101.3 | [W] | Control.Direction | Controls the pump direction | 0 = Forward (CW) 1 = Reverse (CCW) |  | bool |  | - | - | - | - | - | - | -
00101.2 | [W] | Control.ResetFault | Resets alarms and warnings | 0 = No resetting 1 = Reset alarm |  | bool |  | x | x | x | x | x | x | x
00101.1 | [W] | Control.OnOffReq | Set the system on or off | 0 = Off 1 = On |  | bool |  | x x | x x | x x | x x | x x | x x | x x
00101.0 | [W] | Control.RemoteAccessReq | Set local or remote (bus) control | 0 = Local control 1 = Remote control (bus) |  | bool |  | x x | x x |  | x x | x x | x x | x x
00102 | [W] | Control.ControlMode | Set control mode | 0 = Constant speed 1 = Constant frequency 3 = Constant head 4 = Constant pressure 5 = Constant diff. pressure 6 = Proportional pressure 7 = Constant flow 8 = Constant temperature 9 = Constant Differential Temperature 10 = Constant level 128 = AUTOADAPT 129 = FLOWADAPT 130 = Closed loop sensor |  | enum |  | x x x x - (x) - - - - - - - |  |  |  | .- - x x - x - - - - x - - | x x x x x x x x x x - x x | x x x x - x - x x - - x -
00103 | [W] | Control.OperationMode | Set operating mode (Multi-B and DDD fixed to AutoControl) | 0 = AutoControl (Normal) 4 = OpenLoopMinimum 6 = OpenLoopMaximum |  | enum |  | x x x | x - - | x - x | x x x | - | x x x | x x x
00104 | [W] | Control.Setpoint | Set the setpoint in 0.01% |  | 0.01 | % |  | x | x | x | x | X | x | x
00105 | [W] | Control.Pump1 | Used to Manual control pump 1 (not Multi-E) | 0 = Auto 1 = Manual Start 2 = Manual Stop |  | enum |  | x x x | x - x | - | x x x | x x x | - | -
00106 | [W] | Control.Pump2 | Used to manual control pump 2 (not Multi-E) | 0 = Auto 1 = Manual Start 2 = Manual Stop |  | enum |  | x x x | x - x | - | x x x | x x x | - | -
00107 | [W] | Control.Pump3 | Used to manual control pump 3 (not Multi-E) | 0 = Auto 1 = Manual Start 2 = Manual Stop |  | enum |  | x x x | x - x | - | x x x | x x x | - | -
00108 | [W] | Control.Pump4 | Used to manual control pump 4 (not Multi-E) | 0 = Auto 1 = Manual Start 2 = Manual Stop |  | enum |  | x x x | x - x | - | x x x | x x x | - | -
00109 | [W] | Control.Pump5 | Used to manual control pump 5 (not Multi-E or Multi-B) | 0 = Auto 1 = Manual Start 2 = Manual Stop |  | enum |  | x x x | - | - | x x x | x x x | - | -
00110 | [W] | Control.Pump6 | Used to manual control pump 6 (not Multi-E or Multi-B) | 0 = Auto 1 = Manual Start 2 = Manual Stop |  | enum |  | x x x | - | - | x x x | x x x | - | -
00111 | [W] | Control.TankFillStartLimit | Set start limit in tank filling applications (Multi-B only) |  | 0.01 | % |  | - | x |  |  | - | - | -
00112 | [W] | Control.TankFillStopLimit | Set stop limit in tank filling applications (Multi-B only) |  | 0.01 | % |  | - | x |  |  | - | - | -
00113 | [W] | Control.TankFillAlarmHighLimit | Set alarm high limit in tank filling applications (Multi-B only) |  | 0.01 | % |  | - | x |  |  | - | - | -
00114 | [W] | Control.TankFillWarningLowLimit | Set warning low limit in tank filling applications (Multi-B only) |  | 0.01 | % |  | - | x |  |  | - | - | -
00115 | [W] | Control.SetPropControlReduction | Set reduction in % when in proportional pressure mode (MPC only) |  | 0.01 | % |  | x |  |  |  | x | X | -
00116 | [W] | Control.SetPropControlFlowMax | Set manual flow max when in proporional pressure mode (MPC only) |  | 0.1 | m3/h |  | x |  |  |  | x | X | -
00117 | [W] | Control.PilotPump | Used to Manual control the pilot pump (MPC only) | 0 = Auto 1 = Manual Start 2 = Manual Stop |  | enum |  | x - x | - | - |  | - | - | -
00118 | [W] | Control.BackupPump | Used to Manual control the backup pump (MPC only) | 0 = Auto 1 = Manual Start 2 = Manual Stop |  | enum |  | x - x | - | - |  | - | - | -
00119 | [W] | Control.SetpointDDDSensor1 | Set the setpoint of DDD Remote Sensor 1 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00120 | [W] | Control.SetpointDDDSensor2 | Set the setpoint of DDD Remote Sensor 2 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00121 | [W] | Control.SetpointDDDSensor3 | Set the setpoint of DDD Remote Sensor 3 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00122 | [W] | Control.SetpointDDDSensor4 | Set the setpoint of DDD Remote Sensor 4 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00123 | [W] | Control.SetpointDDDSensor5 | Set the setpoint of DDD Remote Sensor 5 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00124 | [W] | Control.SetpointDDDSensor6 | Set the setpoint of DDD Remote Sensor 6 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00125 | [W] | Control.SetpointDDDSensor7 | Set the setpoint of DDD Remote Sensor 7 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00126 | [W] | Control.SetpointDDDSensor8 | Set the setpoint of DDD Remote Sensor 8 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00127 | [W] | Control.SetpointDDDSensor9 | Set the setpoint of DDD Remote Sensor 9 |  | 0.001 | bar |  |  | - | - |  | x | - | -
00128 | [W] | Control.SetpointDDDSensor10 | Set the setpoint of DDD Remote Sensor 10 |  | 0.001 | bar |  |  | - | - |  | x | - | -
00129 | [W] | Control.SystemFeedbackSensor | Selects feedback sensor type according to table 7.6 in MPC GENI profile (MPC only) | 3 = Flow sensor 6 = Pressure sensor |  | enum |  | x | - | - |  | - | - | -
00130 | [W] | Control.SetRemoteSensor1 | Set value of remote sensor 1 to Controller |  | 0.01 | % |  | x | - | - |  | - | - | -
00131 | [W] | Control.SetRemoteSensor2 | Set value of remote sensor 2 to Controller |  | 0.01 | % |  | x | - | - |  | - | - | -
00132 | [W] | Control.SetRemoteSensor3 | Set value of remote sensor 3 to Controller |  | 0.01 | % |  | x | - | - |  | - | - | -
00133 | [W] | Control.SetRemoteSensor4 | Set value of remote sensor 4 to Controller |  | 0.01 | % |  | x | - | - |  | - | - | -
00134 | [W] | Control.SetRemoteSensor5 | Set value of remote sensor 5 to Controller |  | 0.01 | % |  | x | - | - |  | - | - | -
00135 | [W] | Control.SetRemoteSensor6 | Set value of remote sensor 6 to Controller |  | 0.01 | % |  | x | - | - |  | - | - | -
00136 | [W] | Control.SetPump1Speed | Set manual speed of Pump1 |  | 0.01 | % |  | x | - | - |  | x | - | -
00137 | [W] | Control.SetPump2Speed | Set manual speed of Pump2 |  | 0.01 | % |  | x | - | - |  | x | - | -
00138 | [W] | Control.SetPump3Speed | Set manual speed of Pump3 |  | 0.01 | % |  | x | - | - |  | x | - | -
00139 | [W] | Control.SetPump4Speed | Set manual speed of Pump4 |  | 0.01 | % |  | x | - | - |  | x | - | -
00140 | [W] | Control.SetPump5Speed | Set manual speed of Pump5 |  | 0.01 | % |  | x | - | - |  | x | - | -
00141 | [W] | Control.SetPump6Speed | Set manual speed of Pump6 |  | 0.01 | % |  | x | - | - |  | x | - | -
00142 | [W] | Control.SetPilotPumpSpeed | Set manual speed of Pilot Pump |  | 0.01 | % |  | x | - | - |  | - | - | -
00143 | [W] | Control.SetBackupPumpSpeed | Set manual speed of Backup Pump |  | 0.01 | % |  | x | - | - |  | - | - | -
00144 | [W] | Control.SetKp | Set system PI controller proportional gain (ZERO = -10.0) |  | 0.1 |  | 100 | x | - | - |  | x | - | -
00145 | [W] | Control.SetTi | Set system PI controller integral action time |  | 0.1 | s |  | x | - | - |  | x | - | -
00146 | [W] | Control.BusSensorMeasId | Sensor ID for the DDD block of fieldbus sensor meas. (1-10) |  |  | unscaled |  | - | - | - |  | x | - | -
00147 | [W] | Control.BusSensorMeasSeqId | Sequence ID for the DDD block of fieldbus sensor meas. |  |  | unscaled |  | - | - | - |  | x | - | -
00148 | [W] | Control.BusSensorMeasBlockSize | Size of the DDD block of fieldbus sensor meas. (1-8) |  |  | unscaled |  | - | - | - |  | x | - | -
00149 | [W] | Control.BusSensorMeasValue1 | DDD fieldbus sensor measurement 1 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00150 | [W] | Control.BusSensorMeasValue2 | DDD fieldbus sensor measurement 2 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00151 | [W] | Control.BusSensorMeasValue3 | DDD fieldbus sensor measurement 3 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00152 | [W] | Control.BusSensorMeasValue4 | DDD fieldbus sensor measurement 4 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00153 | [W] | Control.BusSensorMeasValue5 | DDD fieldbus sensor measurement 5 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00154 | [W] | Control.BusSensorMeasValue6 | DDD fieldbus sensor measurement 6 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00155 | [W] | Control.BusSensorMeasValue7 | DDD fieldbus sensor measurement 7 |  | 0.001 | bar |  | - | - | - |  | x | - | -
00156 | [W] | Control.BusSensorMeasValue8 | DDD fieldbus sensor measurement 8 |  | 0.001 | bar |  | - | - | - |  | x | - | -
BOOSTER STATUS [R]
00201.15 | [R] | AtMinSpeed | Running at minimum speed (Not Multi-B) | 0 = No 1 = Yes |  | bool |  | x | - | x | x | - | x | x
00201.14 | [R] | RESERVED |  |  |  | bool |  | - | - | - |  | - | - | -
00201.13 | [R] | AtMaxSpeed | Running at maximum speed (Not Multi-B) | 0 = No 1 = Yes |  | bool |  | x | - | x | x | - | x | x
00201.12 | [R] | RESERVED |  |  |  | bool |  |  | - | - |  | - | - | -
00201.11 | [R] | Warning | Warning present | 0 = No 1 = Yes |  | bool |  | x | x | - | x | x | x | x
00201.10 | [R] | Fault | Fault present | 0 = No 1 = Yes |  | bool |  | x | x | x | x | x | x | x
00201.9 | [R] | OnOff | On/Off status of pump/system | 0 = Off 1 = On |  | bool |  | x | x | x | x | x | x | x
00201.8 | [R] | AccessMode | Access Mode status | 0 = Local control 1 = Remote control (bus) |  | bool |  | x | x | x | x | x | x | x
00201.7 | [R] | RESERVED | Direction status | 0 = Forward (CW) 1 = Reverse (CCW) |  | bool |  | - | - | - |  | - | - | -
00201.6 | [R] | Rotation | Rotational status | 0 = No rotation 1 = Rotation |  | bool |  | x | x | x | x | x | x | x
00201.5 | [R] | AtMaxPower | Running at power limit | 0 = No 1 = Yes |  | bool |  | - | - | - |  | - | x | x
00201.4 | [R] | SetpointInfluence | Setpoint influence status | 0 = No influence 1 = Setpoint influence active |  | bool |  | x | - |  | x | x | x | x
00201.3 | [R] | ResetFaultAck | Acknowledge of ResetFault | 0 = No acknowledge 1 = Acknowledged |  | bool |  | x | x | x | x | x | x | x
00201.2 | [R] | ResetAccCountersAck | Acknowledge of ResetAccCounters | 0 = No acknowledge 1 = Acknowledged |  | bool |  | x | - |  |  | x | x | x
00201.1 | [R] | CopyToLocal | Copies remote settings to local settings (Multi-E model H/I only) | 0 = No 1 = Yes |  | bool |  |  | - |  |  |  | x | x
00201.0 | [R] | RESERVED |  |  |  | bool |  |  | -
00202 | [R] | ProcessFeedback | Process value (feedback), in % of sensor range |  | 0.01 | % |  | x | x | x | x | x | x | x
00203 | [R] | ControlMode | Actual control mode | 0 = Constant speed 1 = Constant frequency 3 = Constant head 4 = Constant pressure 5 = Constant diff. pressure 6 = Proportional pressure 7 = Constant flow 8 = Constant temperature 9 = Constant Differential Temperature 10 = Constant level 128 = Automatic Adaptation 129 = FLOWADAPT 130 = Closed loop sensor |  | enum |  | x | x | x |  | x | x | x
00204 | [R] | OperationMode | Actual operating mode | 0 = AutoControl 4 = OpenLoopMinimum 6 = OpenLoopMaximum |  | enum |  | x | x | x | x | x | x | x
00205 | [R] | FaultCode | Grundfos-specific fault code |  |  | enum |  | x | x | x | x | x | x | x
00206 | [R] | WarningCode | Grundfos-specific warning code |  |  | enum |  | x | x |  | x | x | x | x
00208.0 | [R] | PresencePump1 | Presence of pump 1 | 0 = Not present 1 = Present |  | bool |  | x | x | x | x | x | x | x
00208.1 | [R] | PresencePump2 | Presence of pump 2 | 0 = Not present 1 = Present |  | bool |  | x | x | x | x | x | x | x
00208.2 | [R] | PresencePump3 | Presence of pump 3 | 0 = Not present 1 = Present |  | bool |  | x | x | x | x | x | x | -
00208.3 | [R] | PresencePump4 | Presence of pump 4 | 0 = Not present 1 = Present |  | bool |  | x | x | x | x | x | x | -
00208.4 | [R] | PresencePump5 | Presence of pump 5 | 0 = Not present 1 = Present |  | bool |  | x | - | x | x | x | x | -
00208.5 | [R] | PresencePump6 | Presence of pump 6 | 0 = Not present 1 = Present |  | bool |  | x | - | x | x | x | x | -
00208.6 | [R] | PresencePilotPump | Presence of pilot pump | 0 = Not present 1 = Present |  | bool |  | x | -
00208.7 | [R] | PresenceBackupPump | Presence of backup pump | 0 = Not present 1 = Present |  | bool |  | x | -
00209.0 | [R] | RunStatusPump1 | Running status of pump 1 | 0 = Not running 1 = Running |  | bool |  | x | x | x | x | x | x | x
00209.1 | [R] | RunStatusPump2 | Running status of pump 2 | 0 = Not running 1 = Running |  | bool |  | x | x | x | x | x | x | x
00209.2 | [R] | RunStatusPump3 | Running status of pump 3 | 0 = Not running 1 = Running |  | bool |  | x | x | x | x | x | x | -
00209.3 | [R] | RunStatusPump4 | Running status of pump 4 | 0 = Not running 1 = Running |  | bool |  | x | x | x | x | x | x | -
00209.4 | [R] | RunStatusPump5 | Running status of pump 5 | 0 = Not running 1 = Running |  | bool |  | x | - | x | x | x | x | -
00209.5 | [R] | RunStatusPump6 | Running status of pump 6 | 0 = Not running 1 = Running |  | bool |  | x | - | x | x | x | x | -
00209.6 | [R] | RunStatusPilotPump | Running status of pilot pump | 0 = Not running 1 = Running |  | bool |  | x | -
00209.7 | [R] | RunStatusBackupPump | Running status of backup pump | 0 = Not running 1 = Running |  | bool |  | x | -
00210.0 | [R] | FaultPump1 | Fault on pump 1 | 0 = No Fault 1 = Fault |  | bool |  | x | x | x | x | x | x | x
00210.1 | [R] | FaultPump2 | Fault on pump 2 | 0 = No Fault 1 = Fault |  | bool |  | x | x | x | x | x | x | x
00210.2 | [R] | FaultPump3 | Fault on pump 3 | 0 = No Fault 1 = Fault |  | bool |  | x | x | x | x | x | x | -
00210.3 | [R] | FaultPump4 | Fault on pump 4 | 0 = No Fault 1 = Fault |  | bool |  | x | x | x | x | x | x | -
00210.4 | [R] | FaultPump5 | Fault on pump 5 | 0 = No Fault 1 = Fault |  | bool |  | x | - | x | x | x | x | -
00210.5 | [R] | FaultPump6 | Fault on pump 6 | 0 = No Fault 1 = Fault |  | bool |  | x | - | x | x | x | x | -
00210.6 | [R] | FaultPilotPump | Fault on pilot pump | 0 = No Fault 1 = Fault |  | bool |  | x | -
00210.7 | [R] | FaultBackupPump | Fault on backup pump | 0 = No Fault 1 = Fault |  | bool |  | x | -
00211.0 | [R] | CommFaultPump1 | Communication fault pump 1 | 0 = Communication OK (or not present) 1 = Communication fault |  | bool |  | x | x | x | x | x | x | x
00211.1 | [R] | CommFaultPump2 | Communication fault pump 2 | 0 = Communication OK (or not present) 1 = Communication fault |  | bool |  | x | x | x | x | x | x | x
00211.2 | [R] | CommFaultPump3 | Communication fault pump 3 | 0 = Communication OK (or not present) 1 = Communication fault |  | bool |  | x | x | x | x | x | x | -
00211.3 | [R] | CommFaultPump4 | Communication fault pump 4 | 0 = Communication OK (or not present) 1 = Communication fault |  | bool |  | x | x | x | x | x | x | -
00211.4 | [R] | CommFaultPump5 | Communication fault pump 5 | 0 = Communication OK (or not present) 1 = Communication fault |  | bool |  | x | - | x | x | x | x | -
00211.5 | [R] | CommFaultPump6 | Communication fault pump 6 | 0 = Communication OK (or not present) 1 = Communication fault |  | bool |  | x | - | x | x | x | x | -
00211.6 | [R] | CommFaultPilotPump | Communication fault on pilot pump | 0 = Communication OK (or not present) 1 = Communication fault |  | bool |  | x | -
00211.7 | [R] | CommFaultBackupPump | Communication fault on backup pump | 0 = Communication OK (or not present) 1 = Communication fault |  | bool |  | x | -
00212.0 | [R] | RESERVED | [5 empty] | x | - |  |  | x
00212.1 | [R] | SystemActiveFunction.EmergencyRun | Emergency run (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | - |  |  | x
00212.2 | [R] | SystemActiveFunction.StandbyPumps | Standby pump(s) running (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | - |  |  | x
00212.3 | [R] | SystemActiveFunction.PumpTestRun | Pump test run (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | - |  |  | x
00212.4 | [R] | SystemActiveFunction.AlternativeSetpoint | Alternative setpoint in use (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | - |  |  | x
00212.5 | [R] | SystemActiveFunction.ClockProgram | Clock program (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | - |  |  | x
00212.6 | [R] | SystemActiveFunction.RemoteVNC | Virtual Network Connection active (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | - |  |  | x
00212.7 | [R] | SystemActiveFunction.RemoteBus | Remote bus (CU 35x and Multi-B) | 0 = Inactive 1 = Active |  | bool |  | x | x |  |  | x
00212.8 | [R] | SystemActiveFunction.RemoteServicePort | Service port in use (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | - |  |  | x
00212.9 | [R] | SystemActiveFunction.PressureRelief | Pressure relief (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | -
00212.10 | [R] | SystemActiveFunction.SoftPressure | Soft pressure (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | -
00212.11 | [R] | SystemActiveFunction.LowFlowBoost | Low flow boost (CU 35x and CU 323 Multi-B only) | 0 = Inactive 1 = Active |  | bool |  | x | - |  |  | x
00212.12 | [R] | SystemActiveFunction.LowFlowStop | Low flow stop (CU 35x and CU 323 Multi-B) | 0 = Inactive 1 = Active |  | bool |  | x | x | x |  | x
00212.13 | [R] | SystemActiveFunction.ProportionalPressure | Running proportional pressure (CU 35x only) | 0 = Inactive 1 = Active |  | bool |  | x | - |  |  | x
00213.0 | [R] | AutoModePump1 | Auto mode control pump 1 (CU 35x only) | 0 = Forced / Manual 1 = Auto control |  | bool |  | x | - |  |  | x
00213.1 | [R] | AutoModePump2 | Auto mode control pump 2 (CU 35x only) | 0 = Forced / Manual 1 = Auto control |  | bool |  | x | - |  |  | x
00213.2 | [R] | AutoModePump3 | Auto mode control pump 3 (CU 35x only) | 0 = Forced / Manual 1 = Auto control |  | bool |  | x | - |  |  | x
00213.3 | [R] | AutoModePump4 | Auto mode control pump 4 (CU 35x only) | 0 = Forced / Manual 1 = Auto control |  | bool |  | x | - |  |  | x
00213.4 | [R] | AutoModePump5 | Auto mode control pump 5 (CU 35x only) | 0 = Forced / Manual 1 = Auto control |  | bool |  | x | - |  |  | x
00213.5 | [R] | AutoModePump6 | Auto mode control pump 6 (CU 35x only) | 0 = Forced / Manual 1 = Auto control |  | bool |  | x | - |  |  | x
00213.6 | [R] | AutoModePilotPump | Auto mode control pilot pump (CU 35x only) | 0 = Forced / Manual 1 = Auto control |  | bool |  | x
00213.7 | [R] | AutoModeBackupPump | Auto mode control backup pump (CU 35x only) | 0 = Forced / Manual 1 = Auto control |  | bool |  | x
00214 | [R] | ApplicationType | System application type status (CU 35x MPC only) | 0 = Unknown 1 = Pressure boosting 2 = Heating pumps on hot side 3 = Heating pumps on cold side 4 = AirCon pumps on hot side 5 = AirCon pumps on cold side 6 = MPC S2000 heating pumps on hot side 7 = MPC S2000 heating pumps on cold side 8 = MPC S2000 AirCon pumps on hot side 9 = MPC S2000 AirCon pumps on cold side 10 = Tank filling 11 = Tank filling (Switches) 255 = Unknown 65535 = Unknown |  | enum |  | x | x
00215 | [R] | TankFillTankHeight | Actual tank height in tank filling applications (Multi-B only) |  | 0.01 | m |  |  | x
00216 | [R] | TankFillStartLimit | Actual start limit in tank filling applications (Multi-B only) |  | 0.01 | % |  |  | x
00217 | [R] | TankFillStopLimit | Actual stop limit in tank filling applications (Multi-B only) |  | 0.01 | % |  |  | x
00218 | [R] | TankFillAlarmHighLimit | Actual alarm high limit in tank filling applications (Multi-B only) |  | 0.01 | % |  |  | x
00219 | [R] | TankFillWarningLowLimit | Actual warning low limit in tank filling applications (Multi-B only) |  | 0.01 | % |  |  | x
00220 | [R] | FeedBackSensorUnit | Unit of feed back sensor | 0 = bar 1 = mbar 2 = m 3 = kPa 4 = psi 5 = ft 6 = m3/h 7 = m3/s 8 = ltr/s 9 = gpm 10 = C 11 = F 12 = % 13 = Kelvin 14 = ltr/h 255 = NA |  | enum |  | x | x |  | x | x | x | x
00221 | [R] | FeedBackSensorMin | Minimum of feedback sensor |  | 1 | unit |  | x | x |  | x | x | x | x
00222 | [R] | FeedBackSensorMax | Maximum of feedback sensor |  | 1 | unit |  | x | x |  | x | x | x | x
00223 | [R] | SystemFeedbackSensor | Selected feedback sensor type according to table 7.6 in MPC GENI profile (MPC only) | 3 = Flow sensor 6 = Pressure sensor |  | enum |  | x | - | - |  |  | - | -
00224 | [R] | AnalogIn1Unit | Analogue input 1, AI1, scaling unit | 51 = 0.001 bar 95 = 0.01 m3/h 84 = 0.01 K 110 = 0.01 C 83 = 0.01 m 7 = 1 W 107 = 0.01 % |  | enum |  | x | - | - |  | x | - | -
00225 | [R] | AnalogIn2Unit | Analogue input 2, AI2, scaling unit | 51 = 0.001 bar 95 = 0.01 m3/h 84 = 0.01 K 110 = 0.01 C 83 = 0.01 m 8 = 10 W 12 = 0.1 % |  | enum |  | x | - | - |  | x | - | -
00226 | [R] | AnalogIn3Unit | Analogue input 3, AI3, scaling unit | 51 = 0.001 bar 95 = 0.01 m3/h 84 = 0.01 K 110 = 0.01 C 83 = 0.01 m 8 = 10 W 12 = 0.1 % |  | enum |  | x | - | - |  | x | - | -
00227 | [R] | AnalogIn4Unit | Analogue input 4, AI4, scaling unit | 51 = 0.001 bar 95 = 0.01 m3/h 84 = 0.01 K 110 = 0.01 C 83 = 0.01 m 8 = 10 W 12 = 0.1 % |  | enum |  | x | - | - |  | x | - | -
00228 | [R] | AnalogIn5Unit | Analogue input 5, AI5, scaling unit | 51 = 0.001 bar 95 = 0.01 m3/h 84 = 0.01 K 110 = 0.01 C 83 = 0.01 m 8 = 10 W 12 = 0.1 % |  | enum |  | x | - | - |  | x | - | -
00229 | [R] | AnalogIn6Unit | Analogue input 6, AI6, scaling unit | 51 = 0.001 bar 22 = 0.01 m3/h 84 = 0.01 K 110 = 0.01 C 83 = 0.01 m 8 = 10 W 12 = 0.1 % |  | enum |  | x | - | - |  | x | - | -
00230 | [R] | AnalogIn7Unit | Analogue input 7, AI7, scaling unit | 51 = 0.001 bar 22 = 0.01 m3/h 84 = 0.01 K 110 = 0.01 C 83 = 0.01 m 8 = 10 W 12 = 0.1 % |  | enum |  | x | - | - |  | x | - | -
00231 | [R] | Kp | System PI controller proportional gain, ZERO = -10.0 |  | 0.1 |  | 100 | x | - | - |  | x | - | -
00232 | [R] | Ti | System PI controller integral action time |  | 0.1 | s |  | x | - | - |  | x | - | -
SYSTEM DATA [R]
00301 | [R] | Head | Actual head (See also OutletPressure) |  | 0.001 | bar |  | xs | xs | xs | xs | xs | xs | x
00302 | [R] | VolumeFlow | Actual system flow |  | 0.1 | m³/h |  | xs | - | xs | xs | xs | xs | x
00303 | [R] | RelativePerformance | Performance relative to max for running pumps |  | 0.01 | % |  | x | x | x | x | x | x | x
00306 | [R] | DigitalInput | Digital inputs |  |  | unscaled |  | x | x | x | x | x | x | x
00307 | [R] | DigitalOutput | Digital outputs |  |  | unscaled |  | x | x | x | x | x | x | x
00308 | [R] | ActualSetpoint | Actual setpoint |  | 0.01 | % |  | x | x | x | x | x | x | x
00309 | [R] | MotorCurrent | Motor current (old Multi-E only) |  | 0.1 | A |  | - | - | x | - | - | - | -
00312 | [R] | Power HI | Total power consumption |  | 1 | W |  | x | x | x | x | x | x | x
00313 | [R] | Power LO | [5 empty] | x | x | x | x | x | x | x
00315 | [R] | InletPressure | System inlet pressure relative to atm. pressure (sensor required) |  | 0.001 | bar | 1000 | xs | xs | - | xs | xs | xs | -
00316 | [R] | RemotePressure1 | Pressure at external sensor relative to atm. pressure (sensor required) |  | 0.001 | bar |  | xs | - | - | xs | - | xs | xs
00317 | [R] | StorageTankLevel | Storage Tank level (sensor required) |  | 0.01 | m | 10000 | xs | xs | xs | xs | xs | xs | -
00320 | [R] | RemoteTemp1 | Temperature at external sensor (sensor required) |  | 0.01 | K |  | xs | - | xs | xs | - | xs | -
00321 | [R] | MeasuredData.Conductivity | Conductivity measurement. Note! Multi-E Model K/J only
00322 | [R] | MeasuredData.PHMeasure | PH measurement Note! Not implemented yet
00323 | [R] | MeasuredData.Turbidity | Turbidity measurement Note! Not implemented yet
00325 | [R] | AuxSensorInput | Auxilary sensor input (sensor required) |  | 0.01 | % |  | - | - | xs | - | - | xs | -
00327 | [R] | OperationTime HI | Total operating time |  | 1 | h |  | x | x | x | x | x | x | x
00328 | [R] | OperationTime LO | [5 empty] | x | x | x | x | x | x | x
00329 | [R] | TotalPoweredTime HI | Total powered time (old Multi-E only) |  | 1 | h |  | - | - | x | - | - | - | -
00330 | [R] | TotalPoweredTime LO | [5 empty] | - | - | x | - | - | - | -
00332 | [R] | Energy HI | Total energy consumption |  | 1 | kWh |  | x | x | x | x | x | x | x
00333 | [R] | Energy LO | [5 empty] | x | x | x | x | x | x | x
00334 | [R] | NumberOfStarts HI | Number of starts |  | 1 | starts |  | - | - | - | - | - | - | -
00335 | [R] | NumberOfStarts LO | [5 empty] | - | - | - | - | - | - | -
00337 | [R] | AmbientTemp | Temperature at external sensor |  | 0.01 | K |  | xs | - | - | xs | - | xs | -
00338 | [R] | InletTemp | Inlet water temperature |  | 0.01 | K |  | xs | - | - | xs | - | - | -
00339 | [R] | OutletTemp | Outlet water temperature |  | 0.01 | K |  | xs | - | - | xs | - | - | -
00340 | [R] | TempDifference | Temperature difference |  | 0.01 | K |  | xs | - | - | xs | - | - | -
00341 | [R] | OutletPressure | System outlet pressure |  | 0.001 | bar |  | xs | xs | xs | xs | xs | xs | -
00342 | [R] | FeedTankLevel | Feed tank level |  | 0.01 | m | 10000 | xs | xs | - | xs | xs | xs | -
00343 | [R] | UserSetpoint | Reference before modifications |  | 0.01 | % |  | x | x | - | x | x | x | x
00344 | [R] | AnalogueInfluence | Reference attenuator |  | 0.01 | % |  | x | x | - | x | x | x | x
00345 | [R] | NumberOfPowerOns | Number of times the controller has been powered on |  | 1 | power-ons |  | x | x | - | x | x | - | -
00346 | [R] | SpecificEnergy | Specific energy for the system (flow sensor required) |  | 0.1 | Wh/m³ |  | xs |  | - |  | xs | xs | -
00347 | [R] | SpecificEnergyAverage | Average specific energy for the system (flow sensor required) |  | 0.1 | Wh/m³ |  | xs | - | - |  | xs | - | -
00348 | [R] | FlowMeasurement1 | Flow measurement 1 (CU 352 and CU 354 only), sensor required |  | 0.1 | m3/h |  | xs | - | - |  | xs | - | -
00349 | [R] | FlowMeasurement2 | Flow measurement 2 (CU 352 and CU 354 only), sensor required |  | 0.1 | m3/h |  | xs | - | - |  | xs | - | -
00350 | [R] | FlowMeasurement3 | Flow measurement 3 (CU 352 and CU 354 only), sensor required |  | 0.1 | m3/h |  | xs | - | - |  | xs | - | -
00351 | [R] | PropControlReduction | Reduction in proportional pressure control mode (not Multi-B) |  | 0.01 | % |  | x | - | - |  | x | x | -
00352 | [R] | PropControlFlowMax | Flow max for proportional pressure control mode (not Multi-B) |  | 0.1 | m3/h |  | x | - | - |  | x | x | -
00353 | [R] | RemotePressure2 | Pressure at external sensor relative to atm. pressure (Multi-E model H/I only), sensor required |  | 0.001 | bar |  | - | - | - | xs | - | xs | -
00354 | [R] | RemoteTemp2 | Temperature at external sensor (Multi-E model H/I only), sensor required |  | 0.01 | K |  | - | - | - | xs | - | xs | xs
00355 | [R] | MediumTemp | Fluid temperature (not Multi-B), sensor required |  | 0.01 | K |  | - | - | - |  | - | xs | x
00356 | [R] | DifferentialPressure | Differential Pressure in the system (Multi-E model H/I only), sensor required |  | 0.001 | bar |  | - | - | - |  | - | xs | x
00357 | [R] | DifferentialInletPressure | Differential Inlet Pressure (Multi-E model H/I only), sensor required |  | 0.001 | bar |  | - | - | - |  | - | xs | -
00358 | [R] | DifferentialOutletPressure | Differential Outlet Pressure (Multi-E model H/I only), sensor required |  | 0.001 | bar |  | - | - | - |  | - | xs | x
00359 | [R] | DifferentialRemotePressure | Differential Remote Pressure (Multi-E model H/I only), sensor required |  | 0.001 | bar |  | - | - | - |  | - | xs | -
00360 | [R] | RemoteFlow | Flow at remote flow meter (Multi-E model H/I only), sensor required |  | 0.1 | m³/h |  | - | - | - |  | - | xs | -
00361 | [R] | LatestNightFlowAverage | Shows the average night flow for the latest night period (DDD only) |  | 0.1 | m3/h |  | - | - | - |  | x | - | -
00362 | [R] | LatestNightPressAverage | Shows the average night pressure for the latest night period (DDD only) |  | 0.001 | bar |  | - | - | - |  | x | - | -
00363 | [R] | Volume HI | The pumped volume (not Multi-B), flow sensor required |  | 0.01 | m3 |  | xs | - | - |  | xs | - | -
00364 | [R] | Volume LO | [5 empty] | xs | - | - |  | xs | - | -
00365 | [R] | HeatEnergyCounter HI | Life time accumulated heat energy direction 1 (Multi-E model H/I only), Ext. temp. sensor required. |  | 1 | kWh |  | - | - | - |  | - | xs | xs
00366 | [R] | HeatEnergyCounter LO | [5 empty] | - | - | - |  | - | xs | xs
00367 | [R] | HeatPower HI | Current heat power (Multi-E model H/I/J only), Ext. temp. sensor required. |  | 1 | W |  | - | - | - |  | - | xs | xs
00368 | [R] | HeatPower LO | [5 empty] | - | - | - |  | - | xs | xs
00369 | [R] | HeatDiffTemp | Forward/Return differential temp. (Multi-E model H/I/J only), Ext. temp. sensor required. |  | 0.01 | C |  | - | - | - |  | - | xs | xs
00370 | [R] | HeatEnergyCounter2 HI | Accumulated heat energy direction 2 Multi-E model H/I only, Ext. temp. sensor required. |  | 1 | kWh |  | - | - | - |  | - | xs | xs
00371 | [R] | HeatEnergyCounter2 LO | [5 empty] | - | - | - |  | - | xs | xs
00372 | [R] | Volume1 HI | Pumped volume direction 1, Multi-E model H/I/J only, Ext. flow sensor required |  | 0.01 | m3 |  | - | - | - |  | - | xs | xs
00373 | [R] | Volume1 LO | [5 empty] | - | - | - |  | - | xs | xs
00374 | [R] | Volume2 HI | Pumped volume direction 2, Multi-E model H/I/J only, Ext. flow sensor required. |  | 0.01 | m3 |  | - | - | - |  | - | xs | xs
00375 | [R] | Volume2 LO | [5 empty] | - | - | - |  | - | xs | xs
00376 | [R] | AnalogIn1Value | Scaled value of analogue input 1, AI1 |  | 1 |  |  | xs | - | - |  | xs | - | -
00377 | [R] | AnalogIn2Value | Scaled value of analogue input 2, AI2 |  | 1 |  |  | xs | - | - |  | xs | - | -
00378 | [R] | AnalogIn3Value | Scaled value of analogue input 3, AI3 |  | 1 |  |  | xs | - | - |  | xs | - | -
00379 | [R] | AnalogIn4Value | Scaled value of analogue input 4, AI4 |  | 1 |  |  | xs | - | - |  | xs | - | -
00380 | [R] | AnalogIn5Value | Scaled value of analogue input 5, AI5 |  | 1 |  |  | xs | - | - |  | xs | - | -
00381 | [R] | AnalogIn6Value | Scaled value of analogue input 6, AI6 |  | 1 |  |  | xs | - | - |  | xs | - | -
00382 | [R] | AnalogIn7Value | Scaled value of analogue input 7, AI7 |  | 1 |  |  | xs | - | - |  | xs | - | -
Pump DATA [R]
00401.0 | [R] | Pump1.AccessMode | Actual access mode of pump 1 | 0 = Local 1 = Remote |  | bool |  | x | x | - | x | x | x | x
00401.1 | [R] | Pump1.OnOff | Actual running status of pump 1 | 0 = Off 1 = On |  | bool |  | x | x | x | x | x | x | x
00401.2 | [R] | Pump1.Fault | Actual fault status of pump 1 | 0 = No Fault 1 = Fault |  | bool |  | x | x | x | x | x | x | x
00402 | [R] | Pump1.FaultCode | Grundfos-specific fault code |  |  | enum |  | x | x | x | x | x | x | x
00403 | [R] | Pump1.OperationTime HI | Running time of pump 1 |  | 1 | h |  | x | x | x | x | x | x | x
00404 | [R] | Pump1.OperationTime LO | [5 empty] | x | x | x | x | x | x | x
00405 | [R] | Pump1.Speed | Speed of pump 1 |  | 0.01 | % |  | x | x | - | x | x | x | x
00406 | [R] | Pump1.LineCurrent | Average value of line currents on pump 1 |  | 0.1 | A |  | x | x | - | x | x | x | x
00407 | [R] | Pump1.Power | Power consumption of pump 1 |  | 10 | W |  | x | x | - | x | x | x | x
00408 | [R] | Pump1.MotorTemperature | Motortemperature of pump 1 |  | 0.01 | K |  | x | x | - | x | x | x | x
00409 | [R] | Pump1.ControlSource | Control source of the pump | 0 = Unknown 1 = Setpoint buttons on pump 2 = GENIbus (from controller) 3 = GENIlink (IR)/GENIair (radio) 4 = External control 5= Start/Stop button |  | Enum |  | x | x | - | x | x | x | x
00410 | [R] | RESERVED | [5 empty] | - | - | - | - | - | -
00411.0 | [R] | Pump2.AccessMode | Actual access mode of pump 2 | 0 = Local 1 = Remote |  | bool |  | x | x |  | x | x | x | x
00411.1 | [R] | Pump2.OnOff | Actual running status of pump 2 | 0 = Off 1 = On |  | bool |  | x | x | x | x | x | x | x
00411.2 | [R] | Pump2.Fault | Actual fault status of pump 2 | 0 = No Fault 1 = Fault |  | bool |  | x | x | x | x | x | x | x
00412 | [R] | Pump2.FaultCode | Grundfos-specific fault code |  |  | enum |  | x | x | x | x | x | x | x
00413 | [R] | Pump2.OperationTime HI | Running time of pump 2 |  | 1 | h |  | x | x | x | x | x | x | x
00414 | [R] | Pump2.OperationTime LO | [5 empty] | x | x | x | x | x | x | x
00415 | [R] | Pump2.Speed | Speed of pump 2 |  | 0.01 | % |  | x | x | - | x | x | x | x
00416 | [R] | Pump2.LineCurrent | Average value of line currents on pump 2 |  | 0.1 | A |  | x | x | - | x | x | x | x
00417 | [R] | Pump2.Power | Power consumption of pump 2 |  | 10 | W |  | x | x | - | x | x | x | x
00418 | [R] | Pump2.MotorTemperature | Motortemperature of pump 2 |  | 0.01 | K |  | x | x | - | x | x | x | x
00419 | [R] | Pump2.ControlSource | Control source of the pump | 0 = Unknown 1 = Setpoint buttons on pump 2 = GENIbus (from controller) 3 = GENIlink (IR)/GENIair (radio) 4 = External control 5= Start/Stop button |  | Enum |  | x | - | - | x | x | x | x
00420 | [R] | RESERVED | [5 empty] | - | - | - | - | - | - | -
00421.0 | [R] | Pump3.AccessMode | Actual access mode of pump 3 | 0 = Local 1 = Remote |  | bool |  | x | x |  | x | x | x | -
00421.1 | [R] | Pump3.OnOff | Actual running status of pump 3 | 0 = Off 1 = On |  | bool |  | x | x | x | x | x | x | -
00421.2 | [R] | Pump3.Fault | Actual fault status of pump 3 | 0 = No Fault 1 = Fault |  | bool |  | x | x | x | x | x | x | -
00422 | [R] | Pump3.FaultCode | Grundfos-specific fault code |  |  | enum |  | x | x | x | x | x | x | -
00423 | [R] | Pump3.OperationTime HI | Running time of pump 3 |  | 1 | h |  | x | x | x | x | x | x | -
00424 | [R] | Pump3.OperationTime LO | [5 empty] | x | x | x | x | x | x | -
00425 | [R] | Pump3.Speed | Speed of pump 3 |  | 0.01 | % |  | x | x | - | x | x | x | -
00426 | [R] | Pump3.LineCurrent | Average value of line currents on pump 3 |  | 0.1 | A |  | x | x | - | x | x | x | -
00427 | [R] | Pump3.Power | Power consumption of pump 3 |  | 10 | W |  | x | x | - | x | x | x | -
00428 | [R] | Pump3.MotorTemperature | Motortemperature of pump 3 |  | 0.01 | K |  | x | x | - | x | x | x | -
00429 | [R] | Pump3.ControlSource | Control source of the pump | 0 = Unknown 1 = Setpoint buttons on pump 2 = GENIbus (Controller) 3 = GENIlink (IR)/GENIair (radio) 4 = External control 5= Start/Stop button |  | Enum |  | x | - | - | x | x | x | -
00430 | [R] | RESERVED | [5 empty] | - | - | - | - | - | - | -
00431.0 | [R] | Pump4.AccessMode | Actual access mode of pump 4 | 0 = Local 1 = Remote |  | bool |  | x | x |  | x | x | x | -
00431.1 | [R] | Pump4.OnOff | Actual running status of pump 4 | 0 = Off 1 = On |  | bool |  | x | x | x | x | x | x | -
00431.2 | [R] | Pump4.FaultCode | Actual fault status of pump 4 | 0 = No Fault 1 = Fault |  | bool |  | x | x | x | x | x | x | -
00432 | [R] | Pump4.FaultCode | Grundfos-specific fault code |  |  | enum |  | x | x | x | x | x | x | -
00433 | [R] | Pump4.OperationTime HI | Running time of pump 4 |  | 1 | h |  | x | x | x | x | x | x | -
00434 | [R] | Pump4.OperationTime LO | [5 empty] | x | x | x | x | x | x | -
00435 | [R] | Pump4.Speed | Speed of pump 4 |  | 0.01 | % |  | x | x | - | x | x | x | -
00436 | [R] | Pump4.LineCurrent | Average value of line currents on pump 4 |  | 0.1 | A |  | x | x | - | x | x | x | -
00437 | [R] | Pump4.Power | Power consumption of pump 4 |  | 10 | W |  | x | x | - | x | x | x | -
00438 | [R] | Pump4.MotorTemperature | Motortemperature of pump 4 |  | 0.01 | K |  | x | x | - | x | x | x | -
00439 | [R] | Pump4.ControlSource | Control source of the pump | 0 = Unknown 1 = Setpoint buttons on pump 2 = GENIbus (Controller) 3 = GENIlink (IR)/GENIair (radio) 4 = External control 5= Start/Stop button |  | Enum |  | x | - | - | x | x | x | -
00440 | [R] | RESERVED | [5 empty] | - | - | - | - | - | - | -
00441.0 | [R] | Pump5.AccessMode | Actual access mode of pump 5 | 0 = Local 1 = Remote |  | bool |  | x | - |  | x | x | x | -
00441.1 | [R] | Pump5.OnOff | Actual running status of pump 5 | 0 = Off 1 = On |  | bool |  | x | - | x | x | x | x | -
00441.2 | [R] | Pump5.Fault | Actual fault status of pump 5 | 0 = No Fault 1 = Fault |  | bool |  | x | - | x | x | x | x | -
00442 | [R] | Pump5.FaultCode | Grundfos-specific fault code |  |  | enum |  | x | - | x | x | x | x | -
00443 | [R] | Pump5.OperationTime HI | Running time of pump 5 |  | 1 | h |  | x | - | x | x | x | x | -
00444 | [R] | Pump5.OperationTime LO | [5 empty] | x | - | x | x | x | x | -
00445 | [R] | Pump5.Speed | Speed of pump 5 |  | 0.01 | % |  | x | - | - | x | x | x | -
00446 | [R] | Pump5.LineCurrent | Average value of line currents on pump 5 |  | 0.1 | A |  | x | - | - | x | x | x | -
00447 | [R] | Pump5.Power | Power consumption of pump 5 |  | 10 | W |  | x | - | - | x | x | x | -
00448 | [R] | Pump5.MotorTemperature | Motortemperature of pump 5 |  | 0.01 | K |  | x | - | - | x | x | x | -
00449 | [R] | Pump5.ControlSource | Control source of the pump | 0 = Unknown 1 = Setpoint buttons on pump 2 = GENIbus (Controller) 3 = GENIlink (IR)/GENIair (radio) 4 = External control 5= Start/Stop button |  | Enum |  | x | - | - | x | x | x | -
00450 | [R] | RESERVED | [5 empty] | - | - | - | - | - | - | -
00451.0 | [R] | Pump6.AccessMode | Actual access mode of pump 6 | 0 = Local 1 = Remote |  | bool |  | x | - |  | x | x | x | -
00451.1 | [R] | Pump6.OnOff | Actual running status of pump 6 | 0 = Off 1 = On |  | bool |  | x | - | x | x | x | x | -
00451.2 | [R] | Pump6.Fault | Actual fault status of pump 6 | 0 = No Fault 1 = Fault |  | bool |  | x | - | x | x | x | x | -
00452 | [R] | Pump6.FaultCode | Grundfos-specific fault code |  |  | enum |  | x | - | x | x | x | x | -
00453 | [R] | Pump6.OperationTime HI | Running time of pump 6 |  | 1 | h |  | x | - | x | x | x | x | -
00454 | [R] | Pump6.OperationTime LO | [5 empty] | x | - | - | x | x | x | -
00455 | [R] | Pump6.Speed | Speed of pump 6 |  | 0.01 | % |  | x | - | - | x | x | x | -
00456 | [R] | Pump6.LineCurrent | Average value of line currents on pump 6 |  | 0.1 | A |  | x | - | - | x | x | x | -
00457 | [R] | Pump6.Power | Power consumption of pump 6 |  | 10 | W |  | x | - | - | x | x | x | -
00458 | [R] | Pump6.MotorTemperature | Motortemperature of pump 6 |  | 0.01 | K |  | x | - | - | x | x | x | -
00459 | [R] | Pump6.ControlSource | Control source of the pump | 0 = Unknown 1 = Setpoint buttons on pump 2 = GENIbus (Controller) 3 = GENIlink (IR)/GENIair (radio) 4 = External control 5= Start/Stop button |  | Enum |  | x | - | - | x | x | x | -
00460 | [R] | RESERVED | [5 empty] | x | - | - | - | - | -
00461.0 | [R] | PilotPump.AccessMode | Actual access mode of pilot pump | 0 = Local 1 = Remote |  | bool |  | x
00461.1 | [R] | PilotPump.OnOff | Actual running status of pilot pump | 0 = Off 1 = On |  | bool |  | x
00461.2 | [R] | PilotPump.Fault | Actual fault status of pilot pump | 0 = No Fault 1 = Fault |  | bool |  | x
00462 | [R] | PilotPump.FaultCode | Grundfos-specific fault code |  |  | enum |  | x
00463 | [R] | PilotPump.OperationTime HI | Running time of pilot pump |  | 1 | h |  | x
00464 | [R] | PilotPump.OperationTime LO | [5 empty] | x
00465 | [R] | PilotPump.Speed | Speed of pilot pump |  | 0.01 | % |  | x
00466 | [R] | PilotPump.LineCurrent | Average value of line currents on pilot pump |  | 0.1 | A |  | x
00467 | [R] | PilotPump.Power | Power consumption of pilot pump |  | 10 | W |  | x
00468 | [R] | PilotPump.MotorTemperature | Motortemperature of pilot pump |  | 0.01 | K |  | x
00469 | [R] | PilotPump.ControlSource | Control source of the pump | 0 = Unknown 1 = Setpoint buttons on pump 2 = GENIbus (Controller) 3 = GENIlink (IR)/GENIair (radio) 4 = External control 5= Start/Stop button |  | Enum |  | x
00470 | [R] | RESERVED | [5 empty] | x
[R]
00471.0 | [R] | BackupPump.AccessMode | Actual access mode of backup pump | 0 = Local 1 = Remote |  | bool |  | x
00471.1 | [R] | BackupPump.OnOff | Actual running status of backup pump | 0 = Off 1 = On |  | bool |  | x
00471.2 | [R] | BackupPump.Fault | Actual fault status of backup pump | 0 = No Fault 1 = Fault |  | bool |  | x
00472 | [R] | BackupPump.FaultCode | Grundfos-specific fault code |  |  | enum |  | x
00473 | [R] | BackupPump.OperationTime HI | Running time of backup pump |  | 1 | h |  | x
00474 | [R] | BackupPump.OperationTime LO | [5 empty] | x
00475 | [R] | BackupPump.Speed | Speed of backup pump |  | 0.01 | % |  | x
00476 | [R] | BackupPump.LineCurrent | Average value of line currents on backup pump |  | 0.1 | A |  | x
00477 | [R] | BackupPump.Power | Power consumption of backup pump |  | 10 | W |  | x
00478 | [R] | BackupPump.MotorTemperature | Motor temperature of backup pump |  | 0.01 | K |  | x
00479 | [R] | BackupPump.ControlSource | Control source of the pump | 0 = Unknown 1 = Setpoint buttons on pump 2 = GENIbus (Controller+F61) 3 = GENIlink (IR)/GENIair (radio) 4 = External control 5= Start/Stop button |  | Enum |  | x
00480 | [R] | RESERVED | [5 empty] | x
00481 | [R] | Pump1.Energy | Energy consumption of pump 1 |  | 1 | kWh |  | x | - | - | x | x | x | x
00482 | [R] | Pump2.Energy | Energy consumption of pump 2 |  | 1 | kWh |  | x | - | - | x | x | x | x
00483 | [R] | Pump3.Energy | Energy consumption of pump 3 |  | 1 | kWh |  | x | - | - | x | x | x | -
00484 | [R] | Pump4.Energy | Energy consumption of pump 4 |  | 1 | kWh |  | x | - | - | x | x | x | -
00485 | [R] | Pump5.Energy | Energy consumption of pump 5 |  | 1 | kWh |  | x | - | - | x | x | x | -
00486 | [R] | Pump6.Energy | Energy consumption of pump 6 |  | 1 | kWh |  | x | - | - | x | x | x | -
00487 | [R] | PilotPump.Energy | Energy consumption of pilot pump |  | 1 | kWh |  | x | - | - | x | - | - | -
00488 | [R] | BackupPump.Energy | Energy consumption of backup pump |  | 1 | kWh |  | x | - | - | x | - | - | -
DDD REMOTE SENSOR DATA [R]
00601.0 | [R] | BatteryWarningDDDSensor1 | Battery level warning on DDD remote sensor 1 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00601.1 | [R] | BatteryWarningDDDSensor2 | Battery level warning on DDD remote sensor 2 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00601.2 | [R] | BatteryWarningDDDSensor3 | Battery level warning on DDD remote sensor 3 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00601.3 | [R] | BatteryWarningDDDSensor4 | Battery level warning on DDD remote sensor 4 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00601.4 | [R] | BatteryWarningDDDSensor5 | Battery level warning on DDD remote sensor 5 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00601.5 | [R] | BatteryWarningDDDSensor6 | Battery level warning on DDD remote sensor 6 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00601.6 | [R] | BatteryWarningDDDSensor7 | Battery level warning on DDD remote sensor 7 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00601.7 | [R] | BatteryWarningDDDSensor8 | Battery level warning on DDD remote sensor 8 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00601.8 | [R] | BatteryWarningDDDSensor9 | Battery level warning on DDD remote sensor 9 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00601.9 | [R] | BatteryWarningDDDSensor10 | Battery level warning on DDD remote sensor 10 | 0 = Battery OK 1 = Battery low |  | bool | [5 empty] | x
00602.0 | [R] | PressureLowDDDSensor1 | Pressure below warning limit at DDD remote sensor 1 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00602.1 | [R] | PressureLowDDDSensor2 | Pressure below warning limit at DDD remote sensor 2 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00602.2 | [R] | PressureLowDDDSensor3 | Pressure below warning limit at DDD remote sensor 3 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00602.3 | [R] | PressureLowDDDSensor4 | Pressure below warning limit at DDD remote sensor 4 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00602.4 | [R] | PressureLowDDDSensor5 | Pressure below warning limit at DDD remote sensor 5 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00602.5 | [R] | PressureLowDDDSensor6 | Pressure below warning limit at DDD remote sensor 6 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00602.6 | [R] | PressureLowDDDSensor7 | Pressure below warning limit at DDD remote sensor 7 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00602.7 | [R] | PressureLowDDDSensor8 | Pressure below warning limit at DDD remote sensor 8 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00602.8 | [R] | PressureLowDDDSensor9 | Pressure below warning limit at DDD remote sensor 9 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00602.9 | [R] | PressureLowDDDSensor10 | Pressure below warning limit at DDD remote sensor 10 | 0 = Pressure OK 1 = Pressure low |  | bool | [5 empty] | x
00603.0 | [R] | MissingDataDDDSensor1 | Pressure data missing from DDD remote sensor 1 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00603.1 | [R] | MissingDataDDDSensor2 | Pressure data missing from DDD remote sensor 2 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00603.2 | [R] | MissingDataDDDSensor3 | Pressure data missing from DDD remote sensor 3 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00603.3 | [R] | MissingDataDDDSensor4 | Pressure data missing from DDD remote sensor 4 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00603.4 | [R] | MissingDataDDDSensor5 | Pressure data missing from DDD remote sensor 5 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00603.5 | [R] | MissingDataDDDSensor6 | Pressure data missing from DDD remote sensor 6 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00603.6 | [R] | MissingDataDDDSensor7 | Pressure data missing from DDD remote sensor 7 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00603.7 | [R] | MissingDataDDDSensor8 | Pressure data missing from DDD remote sensor 8 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00603.8 | [R] | MissingDataDDDSensor9 | Pressure data missing from DDD remote sensor 9 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00603.9 | [R] | MissingDataDDDSensor10 | Pressure data missing from DDD remote sensor 10 | 0 = Pressure data not missing 1 = Pressure data missing | [7 empty] | x
00604.0 | [R] | DataWarningDDDSensor1 | Data model warning from DDD remote sensor 1 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00604.1 | [R] | DataWarningDDDSensor2 | Data model warning from DDD remote sensor 2 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00604.2 | [R] | DataWarningDDDSensor3 | Data model warning from DDD remote sensor 3 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00604.3 | [R] | DataWarningDDDSensor4 | Data model warning from DDD remote sensor 4 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00604.4 | [R] | DataWarningDDDSensor5 | Data model warning from DDD remote sensor 5 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00604.5 | [R] | DataWarningDDDSensor6 | Data model warning from DDD remote sensor 6 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00604.6 | [R] | DataWarningDDDSensor7 | Data model warning from DDD remote sensor 7 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00604.7 | [R] | DataWarningDDDSensor8 | Data model warning from DDD remote sensor 8 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00604.8 | [R] | DataWarningDDDSensor9 | Data model warning from DDD remote sensor 9 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00604.9 | [R] | DataWarningDDDSensor10 | Data model warning from DDD remote sensor 10 | 0 = Data model OK 1 = Data model warning | [7 empty] | x
00605 | [R] | PressureYesterdayDDDSensor1 | The pressure from 24 hours ago at DDD remote sensor 1 |  | 0.001 | bar | [5 empty] | x
00606 | [R] | PressureYesterdayDDDSensor2 | The pressure from 24 hours ago at DDD remote sensor 2 |  | 0.001 | bar | [5 empty] | x
00607 | [R] | PressureYesterdayDDDSensor3 | The pressure from 24 hours ago at DDD remote sensor 3 |  | 0.001 | bar | [5 empty] | x
00608 | [R] | PressureYesterdayDDDSensor4 | The pressure from 24 hours ago at DDD remote sensor 4 |  | 0.001 | bar | [5 empty] | x
00609 | [R] | PressureYesterdayDDDSensor5 | The pressure from 24 hours ago at DDD remote sensor 5 |  | 0.001 | bar | [5 empty] | x
00610 | [R] | PressureYesterdayDDDSensor6 | The pressure from 24 hours ago at DDD remote sensor 6 |  | 0.001 | bar | [5 empty] | x
00611 | [R] | PressureYesterdayDDDSensor7 | The pressure from 24 hours ago at DDD remote sensor 7 |  | 0.001 | bar | [5 empty] | x
00612 | [R] | PressureYesterdayDDDSensor8 | The pressure from 24 hours ago at DDD remote sensor 8 |  | 0.001 | bar | [5 empty] | x
00613 | [R] | PressureYesterdayDDDSensor9 | The pressure from 24 hours ago at DDD remote sensor 9 |  | 0.001 | bar | [5 empty] | x
00614 | [R] | PressureYesterdayDDDSensor10 | The pressure from 24 hours ago at DDD remote sensor 10 |  | 0.001 | bar | [5 empty] | x
00615 | [R] | ActualSetpointDDDSensor1 | The pressure setpoint at DDD remote sensor 1 |  | 0.001 | bar | [5 empty] | x
00616 | [R] | ActualSetpointDDDSensor2 | The pressure setpoint at DDD remote sensor 2 |  | 0.001 | bar | [5 empty] | x
00617 | [R] | ActualSetpointDDDSensor3 | The pressure setpoint at DDD remote sensor 3 |  | 0.001 | bar | [5 empty] | x
00618 | [R] | ActualSetpointDDDSensor4 | The pressure setpoint at DDD remote sensor 4 |  | 0.001 | bar | [5 empty] | x
00619 | [R] | ActualSetpointDDDSensor5 | The pressure setpoint at DDD remote sensor 5 |  | 0.001 | bar | [5 empty] | x
00620 | [R] | ActualSetpointDDDSensor6 | The pressure setpoint at DDD remote sensor 6 |  | 0.001 | bar | [5 empty] | x
00621 | [R] | ActualSetpointDDDSensor7 | The pressure setpoint at DDD remote sensor 7 |  | 0.001 | bar | [5 empty] | x
00622 | [R] | ActualSetpointDDDSensor8 | The pressure setpoint at DDD remote sensor 8 |  | 0.001 | bar | [5 empty] | x
00623 | [R] | ActualSetpointDDDSensor9 | The pressure setpoint at DDD remote sensor 9 |  | 0.001 | bar | [5 empty] | x
00624 | [R] | ActualSetpointDDDSensor10 | The pressure setpoint at DDD remote sensor 10 |  | 0.001 | bar | [5 empty] | x
00625 | [R] | UNIXlatestDataTimeDDDSensor1HI | Latest data received timestamp from sensor 1 |  | 1 | s | [5 empty] | x
00626 | [R] | UNIXlatestDataTimeDDDSensor1LO | [9 empty] | x
00627 | [R] | UNIXlatestDataTimeDDDSensor2HI | Latest data received timestamp from sensor 2 |  | 1 | s | [5 empty] | x
00628 | [R] | UNIXlatestDataTimeDDDSensor2LO | [9 empty] | x
00629 | [R] | UNIXlatestDataTimeDDDSensor3HI | Latest data received timestamp from sensor 3 |  | 1 | s | [5 empty] | x
00630 | [R] | UNIXlatestDataTimeDDDSensor3LO | [9 empty] | x
00631 | [R] | UNIXlatestDataTimeDDDSensor4HI | Latest data received timestamp from sensor 4 |  | 1 | s | [5 empty] | x
00632 | [R] | UNIXlatestDataTimeDDDSensor4LO | [9 empty] | x
00633 | [R] | UNIXlatestDataTimeDDDSensor5HI | Latest data received timestamp from sensor 5 |  | 1 | s | [5 empty] | x
00634 | [R] | UNIXlatestDataTimeDDDSensor5LO | [9 empty] | x
00635 | [R] | UNIXlatestDataTimeDDDSensor6HI | Latest data received timestamp from sensor 6 |  | 1 | s | [5 empty] | x
00636 | [R] | UNIXlatestDataTimeDDDSensor6LO | [9 empty] | x
00637 | [R] | UNIXlatestDataTimeDDDSensor7HI | Latest data received timestamp from sensor 7 |  | 1 | s | [5 empty] | x
00638 | [R] | UNIXlatestDataTimeDDDSensor7LO | [9 empty] | x
00639 | [R] | UNIXlatestDataTimeDDDSensor8HI | Latest data received timestamp from sensor 8 |  | 1 | s | [5 empty] | x
00640 | [R] | UNIXlatestDataTimeDDDSensor8LO | [9 empty] | x
00641 | [R] | UNIXlatestDataTimeDDDSensor9HI | Latest data received timestamp from sensor 9 |  | 1 | s | [5 empty] | x
00642 | [R] | UNIXlatestDataTimeDDDSensor9LO | [9 empty] | x
00643 | [R] | UNIXlatestDataTimeDDDSensor10HI | Latest data received timestamp from sensor 10 |  | 1 | s | [5 empty] | x
00644 | [R] | UNIXlatestDataTimeDDDSensor10LO | [9 empty] | x
SIMULATION [R/W]
00701 | [W] | Simulation.AlarmCode | Alarm simulation Multi-E ('0' clears alarms) |  |  | enum | [6 empty] | x | x
00702 | [W] | Simulation.WarningCode | Warning simulation Multi-E ('0' clears warnings) |  |  | enum | [6 empty] | x | x
00703 | [W] | Simulation.EventCode | MPC only |  |  | enum |  | x | x |  | x | x
00704 | [W] | Simulation.DeviceType | MPC only |  |  | enum |  | x | x |  | x | x
00705 | [W] | Simulation.DeviceNumber | MPC only |  |  | enum |  | x | x |  | x | x
00706 | [W] | Simulation.ActionType | MPC only |  |  | enum |  | x |  |  | x | x
00707 | [W] | Simulation.ResetType | MPC only |  |  | enum |  | x |  |  | x | x
00708 | [W] | Simulation.Activate | Activate alarm simulation. |  |  | bool |  | x x | x |  | x | x | x | x
00709 | [R] | Simulation.Active | Status of alarm/warning simulation |  |  | bool |  | x | x |  | x | x | x | x
USER REGISTERS [R/W]
00751 | [R/W] | UserLabel1 |  |  |  | unscaled |  | x | x | x | x | x | x | x
00752 | [R/W] | UserLabel2 |  |  |  | unscaled |  | x | x | x | x | x | x | x
00753 | [R/W] | UserLabel3 |  |  |  | unscaled |  | x | x | x | x | x | x | x
00754-00799 | [R/W] | UserLabel4...UserLabel49 |  |  |  | unscaled |  | x | x | x | x | x | x | x
00800 | [R/W] | UserLabel50 |  |  |  | unscaled |  | x | x | x | x | x | x | x

## IO 270
GRUNDFOS CIM 200/260/500 MODBUS PROFILE for IO 270 in a CIU 201/261/501
Sheet version: V02.07.11
Change date (d-m-y): 28-03-2022
All addresses are registers (16 bit), and the address is written in decimal format.
Reg. addr. | Access | Modbus parameter name | Description | Bool/Enum description | Modbus Scale | Modbus Unit
IO 270 REGISTERS [R/W]
01201 | [W] | IO270_SetAnalogOutput | Control of analog output value (Value change triggered) |  | 0.1 | %
01202 | [W] | IO270_SetRelayOutput | Control of output relay (Value change triggered) | 0=Open relay 1=Close relay |  | bool
01203.0 | [W] | IO270_LevelShiftCountControl_bit0 | Clear DI1 duration counters (Rising edge triggered). | 0=No reset 1=Reset counters |  | bool
01203.1 | [W] | IO270_LevelShiftCountControl_bit1 | Clear DI1 shift counter (Rising edge triggered). | 0=No reset 1=Reset counters |  | bool
01203.2 | [W] | IO270_LevelShiftCountControl_bit2 | Clear DI2 duration counters (Rising edge triggered). | 0=No reset 1=Reset counters |  | bool
01203.3 | [W] | IO270_LevelShiftCountControl_bit3 | Clear DI2 shift counter (Rising edge triggered). | 0=No reset 1=Reset counters |  | bool
01203.4 | [W] | IO270_LevelShiftCountControl_bit4 | Clear DI3 duration counters (Rising edge triggered). | 0=No reset 1=Reset counters |  | bool
01203.5 | [W] | IO270_LevelShiftCountControl_bit5 | Clear DI3 shift counter (Rising edge triggered). | 0=No reset 1=Reset counters |  | bool
01203.6 | [W] | IO270_LevelShiftCountControl_bit6 | Clear DI4 duration counters (Rising edge triggered). | 0=No reset 1=Reset counters |  | bool
01203.7 | [W] | IO270_LevelShiftCountControl_bit7 | Clear DI4 shift counter (Rising edge triggered). | 0=No reset 1=Reset counters |  | bool
01211.0 | [R] | IO270_AnalogIn1Fault_bit0 | Analog input 1 sensor signal current too high (>20mA) | 1=Signal current too high (> 20mA) |  | bool
01211.1 | [R] | IO270_AnalogIn1Fault_bit1 | Analog input 1 sensor signal current too low (<4mA) | 1=Signal current too low (< 4mA) |  | bool
01211.2 | [R] | IO270_AnalogIn1Fault_bit2 | Analog input 1 sensor signal voltage too high | 1=Signal voltage too high |  | bool
01211.3 | [R] | IO270_AnalogIn1Fault_bit3 | Analog input 1 sensor power supply fault | 1=Sensor power supply fault |  | bool
01212.0 | [R] | IO270_AnalogIn2Fault_bit0 | Analog input 2 sensor signal current too high (>20mA) | 1=Signal current too high (> 20mA) |  | bool
01212.1 | [R] | IO270_AnalogIn2Fault_bit1 | Analog input 2 sensor signal current too low (<4mA) | 1=Signal current too low (< 4mA) |  | bool
01212.2 | [R] | IO270_AnalogIn2Fault_bit2 | Analog input 2 sensor signal voltage too high | 1=Signal voltage too high |  | bool
01212.3 | [R] | IO270_AnalogIn2Fault_bit3 | Analog input 2 sensor power supply fault | 1=Sensor power supply fault |  | bool
01213.0 | [R] | IO270_TempInStatus_bit0 | Temperatur sensor missing | 1=Sensor missing |  | bool
01213.1 | [R] | IO270_TempInStatus_bit1 | Temperatur sensor short circuited | 1=Short circuited |  | bool
01213.2 | [R] | IO270_TempInStatus_bit2 | Temperature sensor is PT1000 | 1=PT1000 sensor connected |  | bool
01213.3 | [R] | IO270_TempInStatus_bit3 | Temperature sensor is PT100 | 1=PT100 sensor connected |  | bool
01221.0 | [R] | IO270_DigitalInputs_bit0 | Values of digital input DI1 |  |  | bool
01221.1 | [R] | IO270_DigitalInputs_bit1 | Values of digital input DI2 |  |  | bool
01221.2 | [R] | IO270_DigitalInputs_bit2 | Values of digital input DI3 |  |  | bool
01221.3 | [R] | IO270_DigitalInputs_bit3 | Values of digital input DI4 |  |  | bool
01222 | [R] | IO270_Temperature | PT temperature sensor value. Equals 0xFFFF if no PT sensor. |  | 0.01 | K
01223 | [R] | IO270_AnalogInput1 | AI1 value. Equals 0xFFFF if AI1 not selected on jumpers. |  | 0.1 | %
01224 | [R] | IO270_AnalogInput2 | AI2 value. Equals 0xFFFF if AI2 not selected on jumpers. |  | 0.1 | %
01225 | [R] | IO270_RelayOut | Status of Output relay |  |  | bool
01226 | [R] | IO270_DI1ShiftHighCounterHI | Number of DI1 level shifts from low to high |  |  | unscaled
01227 | [R] | IO270_DI1ShiftHighCounterLO
01228 | [R] | IO270_DI2ShiftHighCounterHI | Number of DI2 level shifts from low to high |  |  | unscaled
01229 | [R] | IO270_DI2ShiftHighCounterLO
01230 | [R] | IO270_DI3ShiftHighCounterHI | Number of DI3 level shifts from low to high |  |  | unscaled
01231 | [R] | IO270_DI3ShiftHighCounterLO
01232 | [R] | IO270_DI4ShiftHighCounterHI | Number of DI4 level shifts from low to high |  |  | unscaled
01233 | [R] | IO270_DI4ShiftHighCounterLO
01234 | [R] | IO270_DI1ShiftLowCounterHI | Number of DI1 level shifts from high to low |  |  | unscaled
01235 | [R] | IO270_DI1ShiftLowCounterLO
01236 | [R] | IO270_DI2ShiftLowCounterHI | Number of DI2 level shifts from high to low |  |  | unscaled
01237 | [R] | IO270_DI2ShiftLowCounterLO
01238 | [R] | IO270_DI3ShiftLowCounterHI | Number of DI3 level shifts from high to low |  |  | unscaled
01239 | [R] | IO270_DI3ShiftLowCounterLO
01240 | [R] | IO270_DI4ShiftLowCounterHI | Number of DI4 level shifts from high to low |  |  | unscaled
01241 | [R] | IO270_DI4ShiftLowCounterLO
01242 | [R] | IO270_DI1HighDurationTotalHI | Total duration of DI1 high level |  | 1 | min
01243 | [R] | IO270_DI1HighDurationTotalLO
01244 | [R] | IO270_DI1HighDurationSinceLastHI | Duration of DI1 high level since last shift |  | 1 | min
01245 | [R] | IO270_DI1HighDurationSinceLastLO
01246 | [R] | IO270_DI2HighDurationTotalHI | Total duration of DI2 high level |  | 1 | min
01247 | [R] | IO270_DI2HighDurationTotalLO
01248 | [R] | IO270_DI2HighDurationSinceLastHI | Duration of DI2 high level since last shift |  | 1 | min
01249 | [R] | IO270_DI2HighDurationSinceLastLO
01250 | [R] | IO270_DI3HighDurationTotalHI | Total duration of DI3 high level |  | 1 | min
01251 | [R] | IO270_DI3HighDurationTotalLO
01252 | [R] | IO270_DI3HighDurationSinceLastHI | Duration of DI3 high level since last shift |  | 1 | min
01253 | [R] | IO270_DI3HighDurationSinceLastLO
01254 | [R] | IO270_DI4HighDurationTotalHI | Total duration of DI4 high level |  | 1 | min
01255 | [R] | IO270_DI4HighDurationTotalLO
01256 | [R] | IO270_DI4HighDurationSinceLastHI | Duration of DI4 high level since last shift |  | 1 | min
01257 | [R] | IO270_DI4HighDurationSinceLastLO
01258 | [R] | IO270_DI1LowDurationTotalHI | Total duration of DI1 low level |  | 1 | min
01259 | [R] | IO270_DI1LowDurationTotalLO
01260 | [R] | IO270_DI1LowDurationSinceLastHI | Duration of DI1 low level since last shift |  | 1 | min
01261 | [R] | IO270_DI1LowDurationSinceLastLO
01262 | [R] | IO270_DI2LowDurationTotalHI | Total duration of DI2 low level |  | 1 | min
01263 | [R] | IO270_DI2LowDurationTotalLO
01264 | [R] | IO270_DI2LowDurationSinceLastHI | Duration of DI2 low level since last shift |  | 1 | min
01265 | [R] | IO270_DI2LowDurationSinceLastLO
01266 | [R] | IO270_DI3LowDurationTotalHI | Total duration of DI3 low level |  | 1 | min
01267 | [R] | IO270_DI3LowDurationTotalLO
01268 | [R] | IO270_DI3LowDurationSinceLastHI | Duration of DI3 low level since last shift |  | 1 | min
01269 | [R] | IO270_DI3LowDurationSinceLastLO
01270 | [R] | IO270_DI4LowDurationTotalHI | Total duration of DI4 low level |  | 1 | min
01271 | [R] | IO270_DI4LowDurationTotalLO
01272 | [R] | IO270_DI4LowDurationSinceLastHI | Duration of DI4 low level since last shift |  | 1 | min
01273 | [R] | IO270_DI4LowDurationSinceLastLO

## MP 204
GRUNDFOS CIM/CIU 200/260/500 MODBUS profile for MP 204
Sheet version: 01.05.04
Change date (d-m-y): 15-10-2018
All addresses are registers (16 bit), and the address is written in decimal format.
Reg. addr. | Access | Modbus parameter name | Description | Bool/Enum description | Modbus Scale | Modbus Unit
DEVICE CONFIG [R/W] - All saved in EEPROM
00001 | [R/W] | Config.SlaveMinimumReplyDelay | For adding a reply delay in ms (used with radio modem) |  | 1 | ms
00002 | [R/W] | RESERVED
00003 | [R/W] | Config.SoftwareDefinedModbusAddress | Set a Modbus slave address to use if the address switches are set to an invalid value (Modbus RTU only). |  |  | unscaled
00004 | [R/W] | Config.ModbusBitRate | If set to software defined, use this bit rate (Modbus RTU only). | 0 = 1200 1 = 2400 2 = 4800 3 = 9600 4 = 19200 5 = 38400 |  | enum
00005 | [R/W] | Config.AutoAckControlBits | Acknowlege behaviour of control bits | 0 = Manual, 1 = Automatic |  | bool
00006 |  | RESERVED
00007 | [R/W] | Config.ScadaCallbackRegister | Register in the master used for unsolicited messages. (GSM/GRPS only) |  |  | unscaled
00008 | [R/W] | Config.NoDataActivityTimeout | The elapsed time with no data activity before the module issues a "GPRS restart". (GSM/GRPS only) |  | 1 | min
00009 | [R/W] | Config.SoftwareDefinedParity | If software defined, use this parity setting (Modbus RTU only). | 0 = No parity 1 = Even parity 2 = Odd parity |  | enum
00010 | [R/W] | Config.SoftwareDefinedStopBit | If software defined, use this stop bit setting (Modbus RTU only). | 0 = Not defined 1 = 1 stop bit 2 = 2 stop bit |  | enum
00011 | [R/W] | Config.ScadaPinCode | Code to use if ScadaPinCode is enabled (GSM/GPRS only)
00013 | [R/W] | Config.GENIbusDiodeOff | Switching off the GENIbus diode (LED2) | 0=On (default) 1=Off |  | bool
DEVICE STATUS [R]
00021 | [R] | GENIbusCRCErrorCnt | CRC error counter on the GENIbus |  |  | unscaled
00022 | [R] | GENIbusDataErrorCnt | Data error counter on the GENIbus |  |  | unscaled
00023 | [R] | VersionNumber | Software version number |  |  | unscaled
00024 | [R] | ActualModbusAddress | Actual modbus slave address (Read only) |  |  | unscaled
00025 | [R] | GENIbusTXcount HI | Transmit counter on GENIbus |  |  | unscaled
00026 | [R] | GENIbusTXcount LO
00027 | [R] | GENIbusRXcount HI | Receive counter on GENIbus |  |  | unscaled
00028 | [R] | GENIbusRXcount LO
00029.0 | [R] | ScadaPinCodeEnabled | Determines if the use of a Scada Pin Code is enabled (GSM/GPRS only) | 0 = Pin code disabled 1 = Pin code enabled
00029.1 | [R] | WriteAccessStatus | Determines if write (control) access is granted or not (GSM/GPRS only) | 0 = No write access 1 = Write access
00029.2 | [R] | LockinBlocked | Login blocked due to too many password attempts | 0 = No Login blocking 1 = Login blocked
00030 | [R] | GrundfosUnitFamily | Grundfos product family | 0 = - 1 = UPE/MAGNA pump 2 = MGE 7 = Motor Protection Unit 17 = Multi-E 21 = MPC / Multi-B 25 = CU 351 - CR Monitor 26 = CU 361 - Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller CU 2X1 255 = N/A |  | enum
00031 | [R] | GrundfosUnitType | Grundfos product type number |  |  | unscaled
00032 | [R] | GrundfosUnitVersion | Grundfos product version number |  |  | unscaled
00033 | [R] | BatteryState | State of CIM 260 battery | 0 = Battery not present 1 = Battery must be replaced 2 = Battery charging 3 = Battery needs charging, but temperature too high 4 = Battery needs charging, but temperature too low 5 = Battery Low 6 = Battery OK 255 = Battery state not available |  | enum
GSM REAL TIME CLOCK [R/W] (ONLY AVAILABLE IN CIM 25X!)
00080 | [W] | SetUNIXRealTimeClockHI | Set Real Time Clock (32 bit UNIX format) (GSM/GPRS only) |  | 1 | s
00081 | [W] | SetUNIXRealTimeClockLO
00082 | [W] | SetRtcSecond | Set Real Time Clock (Seconds) (GSM/GPRS only) |  |  | enum
00083 | [W] | SetRtcMinute | Set Real Time Clock (Minutes) (GSM/GPRS only) |  |  | enum
00084 | [W] | SetRtcHour | Set Real Time Clock (Hours) (GSM/GPRS only) |  |  | enum
00085 | [W] | SetRtcDay | Set Real Time Clock (Day) (GSM/GPRS only) |  |  | enum
00086 | [W] | SetRtcMonth | Set Real Time Clock (Month) (GSM/GPRS only) |  |  | enum
00087 | [W] | SetRtcYear | Set Real Time Clock (Year - after 2000) (GSM/GPRS only) |  |  | enum
00088.0 | [W] | SetRtc | Set Real Time Clock (Normal format) (GSM/GPRS only) | 0 = No command 1 = Set the clock |  | bool
00089 | [R] | Status.UNIXRealTimeClockHI | Real Time Clock (32 bit UNIX format) (GSM/GPRS only) |  | 1 | s
00090 | [R] | Status.UNIXRealTimeClockLO
00091 | [R] | Status.RtcSecond | Real time clock - Seconds (GSM/GPRS only) |  |  | enum
00092 | [R] | Status.RtcMinute | Real time clock - Minutes (GSM/GPRS only) |  |  | enum
00093 | [R] | Status.RtcHour | Real time clock - Hours (GSM/GPRS only) |  |  | enum
00094 | [R] | Status.RtcDay | Real time clock - Day of month (GSM/GPRS only) |  |  | enum
00095 | [R] | Status.RtcMonth | Real time clock - Month (GSM/GPRS only) |  |  | enum
00096 | [R] | Status.RtcYear | Real time clock - Year (after 2000) (GSM/GPRS only) |  |  | enum
00097.0 | [R] | Status.AcknowledgeSetRTC | Acknowledge of Set Real Time Clock command (GSM/GPRS only) | 0 = No acknowledge 1 = Acknowledged |  | bool
MP 204 CONTROL [W]
00101.0 | [R/W] | Control.ResetFault | Control bit that resets alarms and warnings. Rising edge triggered. | 0 = No resetting 1 = Reset alarm |  | bool
00101.1 | [R/W] | Control.Trip | Control bit to command-trip the MP 204. Rising edge triggered. | 0 = No action 1 = Trip |  | bool
00101.2 | [R/W] | Control.OnOffReq | Control bit to switch the pump on and off. Change triggered. | 0 = Off 1 = On |  | bool
00101.3 | [R/W] | Control.ProtectionEnabled | Control bit to enable/disable general protection. Change triggered. | 0 = Disable protection 1 = Enable protection |  | bool
00101.4 | [R/W] | RESERVED |  |  |  | bool
00101.5 | [R/W] | Control.ResetStartCounter | Reset the NumberOfStartsTripCounter. Rising edge triggered. | 0 = No resetting 1 = Reset counter |  | bool
00101.6 | [R/W] | Control.ResetRestartCounter | Reset the AutoRestartsTripCounter. Rising edge triggered. | 0 = No resetting 1 = Reset counter |  | bool
00101.7 | [R/W] | Control.ResetLogs | Reset the max/min voltage and current logs and max number of starts per hour log. Rising edge triggered. | 0 = No resetting 1 = Reset Logs |  | bool
00101.8 | [R/W] | Control.ResetHourCounter | Reset the OperationTimeTripCounter. Rising edge triggered. | 0 = No resetting 1 = Reset counter |  | bool
00101.9 | [R/W] | Control.ResetEnergyCounter | Reset the EnergyTripCounter. Rising edge triggered. | 0 = No resetting 1 = Reset counter |  | bool
MP 204 STATUS [R]
00201.0 | [R] | Status.Rotation | Indicates if the pump is rotating | 0 = No rotation 1 = Rotation |  | bool
00201.1 | [R] | Status.ProtectionEnabled | General protection status | 0 = Protection disabled 1 = Protection enabled |  | bool
00201.2 | [R] | Status.Ready | Ready status | 0 = Not ready 1 = Ready |  | bool
00201.3 | [R] | Status.Fault | Unacknowledged fault status | 0 = No unacknowledged fault 1 = Unacknowledged fault present |  | bool
00201.4 | [R] | Status.PTC | PTC status | 0 = Closed 1 = Open |  | bool
00201.5 | [R] | Status.PhaseSequence | Phase sequence status | 0 = L1-L2-L3 (right) 1 = L3-L2-L1 (left) |  | bool
00202 | [R] | Status.OperatingMode | Actual operating mode | 0 = Started (On) 1 = MotorProtectionTrip 2 = TestTrip 3 = ActuatorStop (Off) |  | enum
00203 | [R] | Status.SystemMode | Actual system mode | 0 = Power up 1 = Operating 2 = MP204 Fault |  | enum
00204 | [R] | Status.AlarmCode | Grundfos-specifc alarm code |  |  | enum
00205.0 | [R] | Status.Warnings1_bit0 | Maximum voltage warning |  |  | bool
00205.1 | [R] | Status.Warnings1_bit1 | Minimum voltage warning |  |  | bool
00205.2 | [R] | Status.Warnings1_bit2 | Maximum line current warning |  |  | bool
00205.3 | [R] | Status.Warnings1_bit3 | Minimum line current warning |  |  | bool
00205.4 | [R] | Status.Warnings1_bit4 | Line current asymmetry warning |  |  | bool
00205.5 | [R] | RESERVED |  |  |  | bool
00205.6 | [R] | RESERVED |  |  |  | bool
00205.7 | [R] | RESERVED |  |  |  | bool
00205.8 | [R] | Status.Warnings1_bit8 | Insulation resistance warning |  |  | bool
00205.9 | [R] | Status.Warnings1_bit9 | Motor temperature (Tempcon) warning |  |  | bool
00205.10 | [R] | Status.Warnings1_bit10 | Motor temperature (PT resistor) warning |  |  | bool
00205.11 | [R] | RESERVED |  |  |  | bool
00205.12 | [R] | Status.Warnings1_bit12 | Maximum cos ϕ warning limit exceeded |  |  | bool
00205.13 | [R] | Status.Warnings1_bit13 | Minimum cos ϕ warning limit exceeded |  |  | bool
00205.14 | [R] | Status.Warnings1_bit14 | Starts per hour warning |  |  | bool
00206.0 | [R] | Status.Warnings2_bit0 | Start capacitor minimum warning |  |  | bool
00206.1 | [R] | Status.Warnings2_bit1 | Run capacitor mininimum warning |  |  | bool
00206.2 | [R] | RESERVED |  |  |  | bool
00206.3 | [R] | Status.Warnings2_bit3 | Tempcon sensor signal fault warning |  |  | bool
00206.4 | [R] | Status.Warnings2_bit4 | Pt sensor signal fault warning |  |  | bool
00206.5 | [R] | Status.Warnings2 bit5 | Service warning: Run trip counter high |  |  | bool
00206.6 | [R] | Status.Warnings2 bit6 | Load continues even if the motor has been switched off |  |  | bool
00207.0 | [R] | Status.Relay1 | Motor control relay status | 0 = Relay opened 1 = Relay closed |  | bool
00207.1 | [R] | Status.Relay2 | Signal relay status | 0 = Relay opened 1 = Relay closed |  | bool
00208.0 | [R] | Status.AckResetFault | Reset fault acknowledge | 0 = No acknowledge 1 = Acknowledged |  | bool
00208.1 | [R] | Status.AckTrip | Trip acknowledge | 0 = No acknowledge 1 = Acknowledged |  | bool
00208.2 | [R] | RESERVED |  |  |  | bool
00208.3 | [R] | RESERVED |  |  |  | bool
00208.4 | [R] | RESERVED |  |  |  | bool
00208.5 | [R] | Status.AckResetStartCounter | Reset Start Counter acknowledge | 0 = No acknowledge 1 = Acknowledged |  | bool
00208.6 | [R] | Status.AckResetRestartCounter | Reset restart counter acknowledge | 0 = No acknowledge 1 = Acknowledged |  | bool
00208.7 | [R] | Status.AckResetLogs | Reset logs acknowledge | 0 = No acknowledge 1 = Acknowledged |  | bool
00208.8 | [R] | Status.AckResetHourCounter | Reset hour counter acknowledge | 0 = No acknowledge 1 = Acknowledged |  | bool
00208.9 | [R] | Status.AckResetEnergyCounter | Reset energy counter acknowledge | 0 = No acknowledge 1 = Acknowledged |  | bool
MP204 DATA [R]
00301 | [R] | MeasuredData.PhaseVoltageL1 | 3-phase: Phase voltage for L1 1-phase: Equals 0 V (reference) |  | 0.1 | V
00302 | [R] | MeasuredData.PhaseVoltageL2 | 3-phase: Phase voltage for L2 1-phase: Phase voltage |  | 0.1 | V
00303 | [R] | MeasuredData.PhaseVoltageL3 | 3-phase: Phase voltage for L3 1-phase: Auxiliary winding voltage |  | 0.1 | V
00304 | [R] | MeasuredData.PhaseVoltageMean | 3-phase: Mean of the phase voltages 1-phase: Phase voltage for L1 |  | 0.1 | V
00305 | [R] | MeasuredData.LineVoltageL1L2 | 3-phase: Voltage between L1-L2 1-phase: Not available |  | 0.1 | V
00306 | [R] | MeasuredData.LineVoltageL2L3 | 3-phase: Voltage between L2-L3 1-phase: Not available |  | 0.1 | V
00307 | [R] | MeasuredData.LineVoltageL3L1 | 3-phase: Voltage between L3-L1 1-phase: Not available |  | 0.1 | V
00308 | [R] | MeasuredData.LineVoltageMean | 3-phase: Mean of the line voltages 1-phase: Not available |  | 0.1 | V
00309 | [R] | MeasuredData.LineCurrentL1 | 3-phase: Line current for line L1 1-phase: Neutral current |  | 0.1 | A
00310 | [R] | MeasuredData.LineCurrentL2 | 3-phase: Line current for line L2 1-phase: Current in mains winding |  | 0.1 | A
00311 | [R] | MeasuredData.LineCurrentL3 | 3-phase: Line current for line L3 1-phase: Current in auxiliary winding |  | 0.1 | A
00312 | [R] | MeasuredData.LineCurrentMean | 3-phase: Mean of the line currents 1-phase: Line current for line L1 |  | 0.1 | A
00313 | [R] | MeasuredData.LineCurrentStart | Line start current measured as the peak of the rms value for a period |  | 0.1 | A
00314 | [R] | MeasuredData.MotorTemp1 | Motor temperature measured by Tempcon |  | 0.01 | K
00315 | [R] | MeasuredData.MotorTemp2 | Motor temperature measured by Pt sensor |  | 0.01 | K
00316 | [R] | MeasuredData.LineCurrentAsym | Line current asymmetry (unbalance) |  | 0.01 | %
00317 | [R] | MeasuredData.CapacitorStart | Start capacitor value |  | 1 | uF
00318 | [R] | MeasuredData.CapacitorRun | Run capacitor value |  | 1 | uF
00319 | [R] | MeasuredData.CapacitorStartRef | Start capacitor reference value |  | 1 | uF
00320 | [R] | MeasuredData.CapacitorRunRef | Run capacitor reference value |  | 1 | uF
00321 | [R] | MeasuredData.LineFrequency | Line frequency |  | 0.1 | Hz
00322 | [R] | MeasuredData.VoltageAngleL1L2 | Voltage angle between the lines L1-L2 |  | 1 | degrees
00323 | [R] | MeasuredData.VoltageAngleL1L3 | Voltage angle between the lines L1-L3 |  | 1 | degrees
00324 | [R] | MeasuredData.CosPhiL1 | Current phase angle cosine for line L1 |  | 0.01
00325 | [R] | MeasuredData.CosPhiL2 | Current phase angle cosine for line L2 |  | 0.01
00326 | [R] | MeasuredData.CosPhiL3 | Current phase angle cosine for line L3 |  | 0.01
00327 | [R] | MeasuredData.CosPhi | Power factor |  | 0.01
00328 | [R] | MeasuredData.Power HI | Power consumption |  | 1 | W
00329 | [R] | MeasuredData.Power LO
00330 | [R] | MeasuredData.Energy HI | Energy consumption |  | 1 | kWh
00331 | [R] | MeasuredData.Energy LO
00332 | [R] | MeasuredData.EnergyTripCounter HI | Energy consumption trip counter |  | 1 | kWh
00333 | [R] | MeasuredData.Energy TripCounter LO
00334 | [R] | MeasuredData.OperationTime HI | Operating time counter |  | 1 | h
00335 | [R] | MeasuredData.OperationTime LO
00336 | [R] | MeasuredData.TotalPoweredTime HI | Power-on time counter |  | 1 | h
00337 | [R] | MeasuredData.TotalPoweredTime LO
00338 | [R] | MeasuredData.OperationTimeTripCounter HI | Operating time trip counter |  | 1 | h
00339 | [R] | MeasuredData.OperationTimeTripCounter LO
00340 | [R] | MeasuredData.NumberOfStarts HI | Number of starts counter |  |  | starts
00341 | [R] | MeasuredData.NumberOfStarts LO
00342 | [R] | MeasuredData.NumberOfStartsTripCounter HI | Number of starts trip counter |  |  | starts
00343 | [R] | MeasuredData.NumberOfStartsTripCounter LO
00344 | [R] | MeasuredData.AutoRestartsTripCounter HI | Number of automatic restarts trip counter |  |  | auto restarts
00345 | [R] | MeasuredData.AutoRestartsTripCounter LO
00346 | [R] | MeasuredData.InsulationResistance | Motor insulation resistance |  | 10 | kOhm
00347 | [R] | MeasuredData.PhaseVoltageDistortion | Phase voltage distortion |  | 0.01 | %
00348 | [R] | MeasuredData.VoltageMaxLog | 3-phase: Logged max line voltage 1-phaser: Logged max phase voltage |  | 0.1 | V
00349 | [R] | MeasuredData.VoltageMinLog | 3-phase: Logged min line voltage 1-phaser: Logged min phase voltage |  | 0.1 | V
00350 | [R] | MeasuredData.CurrentLineMaxLog | Logged maximum line current |  | 0.1 | A
00351 | [R] | MeasuredData.CurrentLineMinLog | Logged minimum line current |  | 0.1 | A
00352 | [R] | MeasuredData.StartsHourMaxLog | Logged maximum number of starts per hour |  |  | starts/h
00353 | [R] | MeasuredData.StartsPerHour | Number of starts per hour |  |  | starts/h
00354 | [R] | MeasuredData.AutoRestartsPer24h | Average rate of auto restarts per 24 hours |  |  | restarts/24h
SIMULATION [R/W]
00701.0 | [R/W] | Simulation.Warnings1_bit0 | Maximum voltage warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.1 | [R/W] | Simulation.Warnings1_bit1 | Minimum voltage warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.2 | [R/W] | Simulation.Warnings1_bit2 | Maximum line current warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.3 | [R/W] | Simulation.Warnings1_bit3 | Minimum line current warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.4 | [R/W] | Simulation.Warnings1_bit4 | Line current asymmetry warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.5 | [R/W] | RESERVED |  |  |  | bool
00701.6 | [R/W] | RESERVED |  |  |  | bool
00701.7 | [R/W] | RESERVED |  |  |  | bool
00701.8 | [R/W] | Simulation.Warnings1_bit8 | Insulation resistance warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.9 | [R/W] | Simulation.Warnings1_bit9 | Motor temperature (Tempcon) warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.10 | [R/W] | Simulation.Warnings1_bit10 | Motor temperature (PT resistor) warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.11 | [R/W] | RESERVED |  |  |  | bool
00701.12 | [R/W] | Simulation.Warnings1_bit12 | Maximum cos ϕ warning limit exceeded. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.13 | [R/W] | Simulation.Warnings1_bit13 | Minimum cos ϕ warning limit exceeded. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00701.14 | [R/W] | Simulation.Warnings1_bit14 | Starts per hour warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00702.0 | [R/W] | Simulation.Warnings2_bit0 | Start capacitor min. warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00702.1 | [R/W] | Simulation.Warnings2_bit1 | Run capacitor min. warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00702.2 | [R/W] | RESERVED |  |  |  | bool
00702.3 | [R/W] | Simulation.Warnings2_bit3 | Tempcon sensor signal fault warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00702.4 | [R/W] | Simulation.Warnings2_bit4 | Pt sensor signal fault warning. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00702.5 | [R/W] | Simulation.Warnings2_bit5 | Service warning: t_run_trip_cnt > t_run_trip_warn. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00702.6 | [R/W] | Simulation.Warnings2_bit6 | Load continues even if the motor has been switched off. Change triggered. | 0 = No simulation 1 = Simulate warning |  | bool
00703.0 | [R/W] | Simulation.Alarms1_bit0 | Maximum voltage alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.1 | [R/W] | Simulation.Alarms1_bit1 | Minimum voltage alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.2 | [R/W] | Simulation.Alarms1_bit2 | Maximum line current alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.3 | [R/W] | Simulation.Alarms1_bit3 | Minimum line current alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.4 | [R/W] | Simulation.Alarms1_bit4 | Line current asymmetry alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.5 | [R/W] | RESERVED |  |  |  | bool
00703.6 | [R/W] | RESERVED |  |  |  | bool
00703.7 | [R/W] | RESERVED |  |  |  | bool
00703.8 | [R/W] | Simulation.Alarms1_bit8 | Insulation resistance alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.9 | [R/W] | Simulation.Alarms1_bit9 | Motor temperature (Tempcon) alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.10 | [R/W] | Simulation.Alarms1_bit10 | Motor temperature (PT resistor) alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.11 | [R/W] | RESERVED |  |  |  | bool
00703.12 | [R/W] | Simulation.Alarms1_bit12 | Maximum cos ϕ alarm limit exceeded. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.13 | [R/W] | Simulation.Alarms1_bit13 | Minimum cos ϕ alarm limit exceeded. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00703.14 | [R/W] | Simulation.Alarms1_bit14 | Starts per hour alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00704.0 | [R/W] | Simulation.Alarms2_bit0 | Start capacitor min. alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00704.1 | [R/W] | Simulation.Alarms2_bit1 | Run capacitor min. alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00704.2 | [R/W] | RESERVED |  |  |  | bool
00704.3 | [R/W] | Simulation.Alarms2_bit3 | Tempcon sensor signal fault alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00704.4 | [R/W] | Simulation.Alarms2_bit4 | Pt sensor signal fault alarm. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00704.5 | [R/W] | Simulation.Alarms2_bit5 | Service alarm: t_run_trip_cnt > t_run_trip_warn. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool
00704.6 | [R/W] | Simulation.Alarms2_bit6 | Load continues even if the motor has been switched off. Change triggered. | 0 = No simulation 1 = Simulate alarm |  | bool

## MixIt
GRUNDFOS MODBUS PROFILE for MixIt
All addresses are registers (16 bit), and the address is written in decimal format.
Sheet version: 01.19
Change date (d-m-y): 14-05-2025
Reg. addr. | Access | Modbus parameter name | Description | Bool/Enum description | Modbus Scale | Modbus Unit | LaUPE / DAB
DEVICE CONFIG [R/W] - All saved in EEPROM
00003 | [R/W] | Config.BusAddress | Configuration of an active Modbus address. Range: 1-247 (factory default: 1). |  |  | enum
00004 | [R/W] | Config.BitRate | Configuration of an active Modbus bit rate(not supported :enum 6 to 8) | 0 = 1200 bits/s 1 = 2400 bits/s 2 = 4800 bits/s 3 = 9600 bits/s (factory default) 4 = 19200 bits/s 5 = 38400 bits/s 6 = 57600 bits/s 7 = 76800 bits/s 8 = 96000 bits/s 9 = 115200 bits/s 255 = Not available / Invalid |  | enum
00005 | [R/W] | Config.AutoAckControlBits | Configuration of control bits | 0 = Rising edge triggered control bits are manually lowered. 1 = Rising edge triggered control bits are automatically lowered, when the module receives the event (factory default). |  | enum
00009 | [R/W] | Config.ModbusParity | Configuration of an active Modbus parity | 0 = No parity (default) 1 = Even parity 2 = Odd parity
00010 | [R/W] | Config.ModbusStopBits | Configuration of an active Modbus stop bit number | 0 = Will default to 1 Stop bit 1 = 1 Stop bit 2 = 2 Stop bits |  | enum
DEVICE STATUS [R]
00023 | [R] | VersionNumber | Modbus software version number (BCD digits 1-4) |  |  | unscaled | x
00030 | [R] | GrundfosUnitFamily | Grundfos product family | 0 = - 1 = MAGNA series 2 = MGE series 7 = Motor Protection Unit 17 = Multi-E booster 21 = MPC / Multi-B 25 = CR Monitor 26 = Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller CU 2X1 47 = MixIt 48 = Level controller LC 2x1 65 = SQ Controller CU 202/302 255 = N/A |  | enum | x
00031 | [R] | GrundfosUnitType | Grundfos product type number |  |  | enum | x
00032 | [R] | GrundfosUnitVersion | Grundfos product version number |  |  | unscaled | x
00034 | [R] | ProductSoftwareVersionHI | Product software version (BCD digit 1-4 aa.bb) |  |  | BCD number
00035 | [R] | ProductSoftwareVersionLO | Product software version (BCD digit 5-8 cc.dd) |  |  | BCD number
00036 | [R] | ProductSoftwareDayMonth | Product software date (BCD ddmm) |  |  | BCD number
00037 | [R] | ProductSoftwareYear | Product software date (BCD yyyy) |  |  | BCD number
00038 | [R] | ProductSoftwareBuildHI | Product software build (BCD digit 1-4) |  |  | BCD number
00039 | [R] | ProductSoftwareBuildLO | Product software version (BCD digit 5) |  |  | BCD number
CONTROL [W]
00101.0 | [W/R] | ControlBits.RemoteAccessReq | Enable/Disable of remote (bus) control | 0 = Remote control disabled 1 = Remote control enabled |  | bool | x x x - - x - - - x - -
00101.1 | [W/R] | ControlBits.OnOff | Starting and stopping of pump (requires Remote mode) | 0 = Off (Stop) 1 = On (Start) |  | bool | x x
00101.2 | [W] | ControlBits.ResetAlarm | Resets alarms and warnings (requires Remote mode) | 0 = No resetting 1 = Reset alarm |  | bool | x x
00101.3 | [W] | ControlBits.ResetAccumulatedCounters | Resets accumulated counters (requires Remote mode) | 0 = No resetting 1 = Reset alarm |  | bool | x
00101.4 | [W/R] | ControlBits.OverHeatProtectionED | Enable/disable of over heat protection (requires Remote mode) | 0 = Over heat protection disabled 1 = Over heat protection enabled |  | bool
00101.5 | [W/R] | ControlBits.FrostProtectionED | Enable/disable of frost protection (requires Remote mode) | 0 = frost protection disabled 1 = frost protection enabled |  | bool
00101.6 | [W/R] | ControlBits.BusFeedbackED | Enable/disable of bus feedback (requires Remote mode) | 0 = Bus feedback disabled 1 = Bus feedback enabled |  | bool
00101.7 | [W] | ControlBits.FrostProtectionCoolED | Enable/disable of frost protection for cooling mode (requires Remote mode) | 0 = frost protection disabled 1 = frost protection enabled |  | bool | bool
00102 | [W/R] | Control.SetTempSetpointRemote | Temperature setpoint via fieldbus (requires Remote mode) |  | 0.01 | K
00103 | [W/R] | Control.SetOutdoorTempRemote | Outdoor temperature value via fieldbus (requires Remote mode) |  | 0.01 | K
00104 | [W/R] | Control.SetUnixRtcHI | Set the Real Time Clock (32 bit UNIX format) |  | 1 | s
00105 | [W/R] | Control.SetUnixRtcLO
00106.0 | [R/W] | ConfigBits.SupplyFlowLimitingED | Enable/disable of supply flow limiting (under license) | 0 = Supply flow limiting disabled 1 = Supply flow limiting enabled |  | bool
00106.1 | [R/W] | ConfigBits.ThermalPowerLimitingED | Enable/disable of thermal power limiting (under license) | 0 = Thermal power limiting disabled 1 = Thermal power limiting enabled |  | bool
00106.2 | [R/W] | ConfigBits.ReturnTempLimitingED | Enable/disable of return temp limiting (under license) | 0 = Return temp. limiting disabled 1 = Return temp. limiting enabled |  | bool
00106.3 | [R/W] | ConfigBits.PrimaryDeltaTLimitingED | Enable/disable of primary delta T limiting (under license) | 0 = Primary delta T limiting disabled 1 = Primary delta T limiting enabled |  | bool
00107 | [R/W] | Config.SupplyFlowLimit | Set supply flow limit (under license) |  | 0.1 | m3/h
00108 | [R/W] | Config.ThermalPowerLimit | Set thermal power limit (under license) |  | 1 | kW
00109 | [R/W] | Config.ReturnTempLimit | Set return temp limit (under license) |  | 0.01 | K
00110 | [R/W] | Config.PrimaryDeltaTLimit | Set primary delta t limit (under license) |  | 0.01 | K
00111 | [W/R] | Config.ManualValveFunction | Set the Manual valve function | 1= Manual Valve Off 2= Manual Valve 100 % Open 3= Manual Valve 50 % Open 4= Manual Valve 25 % Open 5= Manual Valve Fully Closed |  | enum
00112 | [W/R] | Config.ApplicationType | Set the application type | 0 = Radiator Heating 1 = Floor heating 2 = Heating coil 3 = Cooling coil 255 = Not available / Invalid |  | enum
00113 | [W/R] | Config.PumpControlMode | Set Control mode of pump | 0 = Constant pressure 1 = Proportional pressure (default) 2 = Constant speed 5 = Autoadapt 8 = Constant flow |  | enum
00114 | [W/R] | Config.PumpHeadDutyPoint | Desired pressure duty point for const./prop. pressure |  | 1 | m
00115 | [W/R] | Config.PumpFlowDutyPoint] | Desired flow duty point for proportional pressure and flow limit control |  | 0.1 | m3/h
00116 | [W/R] | Config.PumpSpeedDutyPoint | Desired speed in control mode Constant speed |  | 0.01 | %
00117 | [W/R] | Config.TempSetpointSource | Source of the temperature setpoint | 0 = Local 1 = Analog Input 2 = Fieldbus 3 = Outdoor Temp. Analog Input 4 = Outdoor Temp. Fieldbus 255 = Not available / Invalid |  | enum
00118 | [W/R] | Config.DefaultTempSetpoint | Default temperature setpoint |  | 0.01 | K
00125 | [W/R] | Control.BusTempFeedback | Set bus temperature feedback |  | 0.01 | K
00126 | [W/R] | Config.HeatCurveOffset | configuration of heat curve offset |  | 0.01 | K
00127 | [W/R] | Config.HeatCurveSlope | configuration of heat curve slope [0.4; 2.0] |  | 0.01
00128.0 | [R/W] | ConfigBits.SupplyFlowLimitingCoolED | Enable/disable of supply flow limiting for cooling mode (under license) | 0 = Supply flow limiting disabled 1 = Supply flow limiting enabled |  | bool | bool
00128.1 | [R/W] | ConfigBits.ThermalPowerLimitingCoolED | Enable/disable of thermal power limiting for cooling mode (under license) | 0 = Thermal power limiting disabled 1 = Thermal power limiting enabled |  | bool | bool
00128.2 | [R/W] | ConfigBits.ReturnTempLimitingCoolED | Enable/disable of return temp limiting for cooling mode (under license) | 0 = Return temp. limiting disabled 1 = Return temp. limiting enabled |  | bool | bool
00128.3 | [R/W] | ConfigBits.PrimaryDeltaTLimitingCoolED | Enable/disable of primary delta T limiting for cooling mode (under license) | 0 = Primary delta T limiting disabled 1 = Primary delta T limiting enabled |  | bool | bool
00129 | [R/W] | Config.SupplyFlowLimitCool | Set supply flow limit for cooling mode (under license) |  | 0.1 | m3/h | m3/h
00130 | [R/W] | Config.ThermalPowerLimitCool | Set thermal power limit for cooling mode(under license) |  | 1 | kW | kW
00131 | [R/W] | Config.ReturnTempLimitCool | Set return temp limit for cooling mode(under license) |  | 0.01 | K | K
00132 | [R/W] | Config.PrimaryDeltaTLimitCool | Set primary delta t limit for cooling mode(under license) |  | 0.01 | K | K
00133 | [R/W] | Config.PumpControlModeCool | Set Control mode of pump for cooling mode | 0 = Constant pressure 1 = Proportional pressure (default) 2 = Constant speed 5 = Autoadapt 8 = Constant flow |  | enum | enum
00134 | [R/W] | Config.PumpHeadDutyPointCool | Desired pressure duty point for const./prop. pressure for cooling mode |  | 0.1 | m | m
00135 | [R/W] | Config.PumpFlowDutyPointCool | Desired flow duty point for proportional pressure and flow limit control for cooling mode |  | 0.1 | m3/h | m3/h
00136 | [R/W] | Config.PumpSpeedDutyPointCool | Desired speed in control mode Constant speed for cooling mode |  | 0.01 | % | %
00137 | [R/W] | Config.ThermalApplicationType | Control of thermal regulation mode (requires setpoint source = fieldbus) | 0 = Heating 1 = Cooling |  | enum | enum
00138 | [R/W] | Config.ApplicationTypeCool | Set the application type for cooling mode | 100 = General Cooling 255 = Not available / Invalid |  | enum | enum
00139 | [R/W] | Config.Kp | Set Proportional Gain |  |  | -- | --
00140 | [R/W] | Config.Ti | Set Integral action Time |  |  | s | s
00141 | [R/W] | Config.Kvs | Set Valve Capacity |  | 0.1 | m3/h | m3/h
00142 | [R/W] | Config.OutdoorTemperatureX1 | Set Heatcurve Outdoor Temperature X1 |  | 0.01 | K | K
00143 | [R/W] | Config.SetpointY1 | Set Heatcurve Setpoint Y1 |  | 0.01 | K | K
00144 | [R/W] | Config.OutdoorTemperatureX2 | Set Heatcurve Outdoor Temperature X2 |  | 0.01 | K | K
00145 | [R/W] | Config.SetpointY2 | Set Heatcurve Setpoint Y2 |  | 0.01 | K | K
00146 | [R/W] | Config.OutdoorTemperatureX3 | Set Heatcurve Outdoor Temperature X3 |  | 0.01 | K | K
00147 | [R/W] | Config.SetpointY3 | Set Heatcurve Setpoint Y3 |  | 0.01 | K | K
00148 | [R/W] | Config.OutdoorTemperatureX4 | Set Heatcurve Outdoor Temperature X4 |  | 0.01 | K | K
00149 | [R/W] | Config.SetpointY4 | Set Heatcurve Setpoint Y4 |  | 0.01 | K | K
00150 | [R/W] | Config.OutdoorTemperatureX5 | Set Heatcurve Outdoor Temperature X5 |  | 0.01 | K | K
00151 | [R/W] | Config.SetpointY5 | Set Heatcurve Setpoint Y5 |  | 0.01 | K | K
00152 | [R/W] | Config.ValveMode | Valve Mode | 0 = Injection 2 Way 1 = Mixing 3 Way 2 = Injection 3 Way |  | enum | enum
00153 | [R/W] | Config.HeatingCoolingSelection | Heating Cooling Selection | 0 = Heating 1 = Cooling 2 = Combined |  | enum | enum
STATUS [R] | [6 empty] | -
00201.0 | [R] | Status.ActualRemoteAccess | Remote access status | 0 = Remote control disabled 1 = Remote control enabled |  | bool | x
00201.1 | [R] | Status.Fault | Presence of fault | 0 = No fault 1 = Fault present |  | bool
00201.2 | [R] | Status.Ready | Status of pump ready | 0 = Not ready 1 = Ready |  | bool
00201.3 | [R] | Status.ActualRunStatePump | Status of pump running state | 0 = Not running 1 = Running |  | bool
00201.4 | [R] | Status.FanAndDampersED | Status of Fan and dampers E/D | 0 = Fan and dampers disabled 1 = Fan and dampers enabled |  | bool | x
00201.5 | [R] | Status.BusFeedbackED | Status of bus feedback E/D | 0 = Bus feedback disabled 1 = Bus feedback enabled |  | bool
00202 | [R] | For future use
00203 | [R] | For future use
00204.0 | [R] | Status.ReturnTempHigh | Status of Return temperature high warning (under license) | 0 = Ok 1= Return temp. high state |  | bool | x
00204.1 | [R] | Status.ThermalPowerHigh | Status of thermal power high warmimg (under license) | 0 = Ok 1 = Thermal power high state |  | bool
00204.2 | [R] | Status.SupplyFlowHigh | Status of supply flow high warmimg (under license) | 0 = Ok 1 = Supply flow high state |  | bool | x
00204.3 | [R] | Status.FlowTempHigh | Status of flow temperature high warmimg | 0 = Ok 1 = Flow temp. high state |  | bool | x
00204.4 | [R] | Status.CoilFrostRisk | Status of coil frost risk detected warmimg | 0 = Ok 1 = Coil frost risk state |  | bool | x
00204.5 | [R] | Status.DiffTempHigh | Status of differential temp. high warning (under license) | 0 = Ok 1 = Differential temp. high state |  | bool
00205.0 | [R] | Status.HeatCurveDeltaOffsetRangeExceeded | Status of Heat curve delta offset range exceed | 0 = Not exceeded 1 = Exceeded |  | bool
00205.1 | [R] | Status.HeatCurveSlopeFactorRangeExceeded | Status of Heat curve slope factor range exceed | 0 = Not exceeded 1 = Exceeded |  | bool
00205.2 | [R] | Status.HeatCurveSlopeFactorEnabled | Status of Heat curve slope factor enabled | 0 = Not enabled 1 = Enabled |  | bool
00206 | [R] | Status.AlarmCode | MixIt system alarm code |  |  | enum
00207 | [R] | Status.WarningCode | MixIt system warning code |  |  | enum
00208 | [R] | Status.SubAlarmCode | MixIt system subalarm code |  |  | enum
00209 | [R] | Status.SubWarningCode | MixIt system subwarning code |  |  | enum
00210 | [R] | Status.PumpControlMode | Status of pump Control mode | 0 = Constant pressure 1 = Proportional pressure (default) 2 = Constant speed 5 = Autoadapt 8 = Constant flow 255 = Not available / Invalid |  | enum
00211 | [R] | Status.ApplicationType | Application type | 0 = Radiator Heating 1 = Floor heating 2 = Heating coil 3 = Cooling coil 255 = Not available / Invalid |  | enum
00212 | [R] | Status.SystemState | State of the MixIt system | 0 = Powering up (~30s) 1 = Fault (Fault relay activated) 2 = Ready (Ready relay activated) 3 = Preheating heating coil 4 = Temperature control state 5 = Coil frost protection 6 = Floor overheat protection 7 = Shut down due to removal of start signal 8 = Auto Tuner On 9 = Backup control 1, valve 100% open 10= Backup control 2, Return temp. control 255 = Not available / Invalid |  | enum
00216 | [R] | Status.UnixRtcHI | Real Time Clock (32 bit UNIX format) |  | 1 | s | DATA_REAL_TIME_CLOCK
00217 | [R] | Status.UnixRtcLO
00218 | [R] | Status.ApplicationTypeCool | Application type for cooling mode | 100 = General Cooling 255 = Not available / Invalid |  | enum | enum
SYSTEM DATA [R]
00305 | [R] | MeasuredData.HeatPower | Heat transfer power (under license) |  | 1 | kW | x
00306 | [R] | MeasuredData.HeatTempDifference | Heat transfer temperature difference (under license) |  | 0.01 | C
00310 | [R] | MeasuredData.OutdoorTemp | Outdoor temperature |  | 0.01 | K
00311 | [R] | MeasuredData.ActualTempSetpointRemote | Actual temperature setpoint from remote |  | 0.01 | K | x
00312 | [R] | MeasuredData.ActualOutdoorTempRemote | Actual outdoor temperature from remote |  | 0.01 | K
00313 | [R] | MeasuredData.FlowTemp | Flow temperature |  | 0.01 | K | x
00314 | [R] | MeasuredData.SupplyTemp | Supply temperature |  | 0.01 | K
00316 | [R] | MeasuredData.ZoneAirTemp | Zone air temperature |  | 0.01 | K | x
00318 | [R] | MeasuredData.RelativeShuntPress | Relative shunt pressure |  | 0.01 | bar | x
00319 | [R] | MeasuredData.LogicalValveOpening | Logical valve opening |  | 0.01 | %
00320 | [R] | MeasuredData.ValveSupplyFlow | Valve supply flow |  | 0.1 | m3/h
00321 | [R] | MeasuredData.ActualTempSetpoint | Actual temperature setpoint |  | 0.01 | K
00322 | [R] | MeasuredData.Return.Temp | Return.temperature |  | 0.01 | K
00323 | [R] | MeasuredData.Controlled.Temp | Controlled temperature |  | 0.01 | K
00324 | [R] | MeasuredData.BoilerSetpoint | Boiler setpoint |  | 0.01 | K
00325 | [R] | MeasuredData.HeatingEnergyHI | Heating energy, under license |  | 1 | kWh
00326 | [R] | MeasuredData.HeatingEnergyLO
00327 | [R] | MeasuredData.CoolingPower | Cooling power |  | 1 | kW
00334 | [R] | MeasuredData.BusTempFeedback |  |  | 0.01 | K
00335 | [R] | MeasuredData.HeatCurveDeltaOffset | Heat curve delta offset |  | 0.01 | K
00336 | [R] | MeasuredData.HeatCurveSlopeFactor | Heat curve slope factor [0.4; 2.0] |  | 0.01
00339 | [R] | MeasuredData.HeatingVolumeHI | Totally pumped heating volume, under license |  | 0.01 | m3
00340 | [R] | MeasuredData.HeatingVolumeLO
00341 | [R] | MeasuredData.CoolingVolumeHI | Totally pumped cooling volume, under license |  | 0.01 | m3
00342 | [R] | MeasuredData.CoolingVolumeLO
00343 | [R] | MeasuredData.CoolingEnergyHI | Total cooling energy, under license |  | 1 | kWh
00344 | [R] | MeasuredData.CoolingEnergyLO
00345 | [R] | MeasuredData.VolWeightAvgT1HeatHI | Total volume weighted average for T1, Heating (Inlet), under license |  | 0.01 | °C m3
00346 | [R] | MeasuredData.VolWeightAvgT1HeatLO
00347 | [R] | MeasuredData.VolWeightAvgT2HeatHI | Total volume weighted average for T2, Heating (Outlet), under license |  | 0.01 | °C m3
00348 | [R] | MeasuredData.VolWeightAvgT2HeatLO
00349 | [R] | MeasuredData.VolWeightAvgT1CoolHI | Total volume weighted average for T1, Cooling (Inlet), under license |  | 0.01 | °C m3
00350 | [R] | MeasuredData.VolWeightAvgT1CoolLO
00351 | [R] | MeasuredData.VolWeightAvgT2CoolHI | Total volume weighted average for T2, Cooling (Outlet), under license |  | 0.01 | °C m3
00352 | [R] | MeasuredData.VolWeightAvgT2CoolLO
PUMP DATA [R]
00401 | [R] | MeasuredData.PumpWarningCode | Pump warning code |  |  | enum
00402 | [R] | MeasuredData.PumpAlarmCode | Pump alarm code |  |  | enum
00404 | [R] | MeasuredData.PumpFlow | Pump flow |  | 0.1 | m3/h | x
00405 | [R] | MeasuredData.PumpHead | Pump head |  | 0.01 | m
00406 | [R] | MeasuredData.PumpPower | Pump power |  | 1 | W
00407 | [R] | MeasuredData.PercentageSpeed | Data.percentage speed |  | 0.01 | %
00408 | [R] | MeasuredData.PumpEnergyHI | Pump energy |  | 1 | kWh
00409 | [R] | MeasuredData.PumpEnergyLO
00410 | [R] | MeasuredData.PumpOperatingHoursHI | Pump operating hours |  | 1 | h
00411 | [R] | MeasuredData.PumpOperatingHoursLO |  |  |  |  | x
00415 | [R] | MeasuredData.MIXITOperatingHoursHI | MIXIT Operating Hours |  | 1 | s | s
00416 | [R] | MeasuredData.MIXITOperatingHoursLO
SIMULATION [R/W]
00701 | [W] | Simulation.EventCode | Write a supported event code (warning or alarm) |  |  | enum
00702 | [W] | Simulation.EventSubCode | Write a supported event subcode (warning or alarm) |  |  | enum
00708 | [W] | Simulation.Activate | Activation of Alarm/Warning simulation (requires Remote mode)+E26 | 0 = Deactivate 1 = Activate |  | bool
00709 | [R] | Simulation.Active | Status of Alarm/Warning simulation | 0 = Deactivated 1 = Activated |  | bool
USER REGISTERS [R/W]
00751 | [R/W] | UserLabel1 |  | For the user to put in a string |  | unscaled | x
00752 | [R/W] | UserLabel2 |  | For the user to put in a string |  | unscaled | x
00753 | [R/W] | UserLabel3 |  | For the user to put in a string |  | unscaled | x
00754-00799 | [R/W] | UserLabel4-UserLabel49 |  | For the user to put in a string |  | unscaled | x
00800 | [R/W] | UserLabel50 |  | For the user to put in a string |  | unscaled | x

## CIU xx2 AutoAdapt
GRUNDFOS MODBUS PROFILE for CIU 202/262/502 AutoAdapt
All addresses are registers (16 bit), and the address is written in decimal format.
Sheet version: 01.05.06
Change date (d-m-y): 01-08-2018
Reg. addr. | Access | Modbus parameter name | Description | Bool/Enum description | Modbus Scale | Modbus Unit
DEVICE CONFIG [R/W] - All saved in EEPROM
00001 | [R/W] | Config.SlaveMinimumReplyDelay | For adding a reply delay in ms |  | 1 | ms
00002 | [R/W] | RESERVED
00003 | [R/W] | Config.SoftwareDefinedModbusAddress | Set a Modbus slave address to use if the address switches are set to an invalid value (Modbus RTU only). |  |  | unscaled
00004 | [R/W] | Config.ModbusBitRate | If set to software defined, use this bit rate (Modbus RTU only). | 0 = 1200 1 = 2400 2 = 4800 3 = 9600 4 = 19200 5 = 38400 |  | enum
00005 | [R/W] | Config.AutoAckControlBits | Acknowlege behaviour of control bits | 0 = Manual 1 = Automatic |  | bool
00006 | [R/W] | Config.ReadWriteSeparation | Separate reads from writes | 0 = No separation 1 = Separate registers |  | bool
00007 | [R/W] | Config.ScadaCallbackRegister | Register in the master used for unsolicited messages. (GSM/GRPS only) |  |  | unscaled
00008 | [R/W] | Config.NoDataActivityTimeout | The elapsed time with no data activity before the module issues a "GPRS restart". (GSM/GRPS only) |  | 1 | min
00009 | [R/W] | Config.SoftwareDefinedParity | If software defined, use this parity setting (Modbus RTU only). | 0 = No parity 1 = Even parity 2 = Odd parity |  | enum
00010 | [R/W] | Config.SoftwareDefinedStopBit | If software defined, use this stop bit setting (Modbus RTU only). | 0 = Not defined 1 = 1 stop bit 2 = 2 stop bit |  | enum
00011 | [R/W] | Config.ScadaPinCode | Code to use if ScadaPinCode is enabled (GSM/GPRS only)
DEVICE STATUS [R]
00021 | [R] | GENIbusCRCErrorCnt | CRC error counter on the GENIbus |  |  | unscaled
00022 | [R] | GENIbusDataErrorCnt | Data error counter on the GENIbus |  |  | unscaled
00023 | [R] | VersionNumber | Software version number |  |  | unscaled
00024 | [R] | ActualModbusAddress | Actual modbus slave address (Read only) |  |  | unscaled
00025 | [R] | GENIbusTXcount HI | Transmit counter on GENIbus |  |  | unscaled
00026 | [R] | GENIbusTXcount LO
00027 | [R] | GENIbusRXcount HI | Receive counter on GENIbus |  |  | unscaled
00028 | [R] | GENIbusRXcount LO
00029.0 | [R] | ScadaPinCodeEnabled | Determines if the use of a Scada Pin Code is enabled (GSM/GPRS only) | 0 = Pin code disabled 1 = Pin code enabled
00029.1 | [R] | WriteAccessStatus | Determines if write (control) access is granted or not (GSM/GPRS only) | 0 = No write access 1 = Write access
00029.2 | [R] | LockinBlocked | Login blocked due to too many password attempts | 0 = No Login blocking 1 = Login blocked
00030 | [R] | GrundfosUnitFamily | Grundfos product family | 0 = - 1 = UPE/MAGNA pump 2 = MGE 7 = Motor Protection Unit 17 = Multi-E 21 = MPC / Multi-B 25 = CU 351 - CR Monitor 26 = CU 361 - Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller CU 2X1 255 = N/A |  | enum
00031 | [R] | GrundfosUnitType | Grundfos product type number |  |  | unscaled
00032 | [R] | GrundfosUnitVersion | Grundfos product version number |  |  | unscaled
00033 | [R] | BatteryState | State of cellular module battery | 0 = Battery not present 1 = Battery must be replaced 2 = Battery charging 3 = Battery needs charging, but temperature too high 4 = Battery needs charging, but temperature too low 5 = Battery Low 6 = Battery OK 255 = Battery state not available |  | enum
00034 | [R] | ProductSoftwareVersionHI | Product software version (BCD digit 1-4 aa.bb) |  |  | BCD number
00035 | [R] | ProductSoftwareVersionLO | Product software version (BCD digit 5-8 cc.dd) |  |  | BCD number
00036 | [R] | ProductSoftwareDayMonth | Product software date (BCD ddmm) |  |  | BCD number
00037 | [R] | ProductSoftwareYear | Product software date (BCD yyyy) |  |  | BCD number
GSM REAL TIME CLOCK [R/W] (ONLY AVAILABLE IN CIM 25X!)
00080 | [W] | SetUNIXRealTimeClockHI | Set Real Time Clock (32 bit UNIX format) (GSM/GPRS only) |  | 1 | s
00081 | [W] | SetUNIXRealTimeClockLO
00082 | [W] | SetRtcSecond | Set Real Time Clock (Seconds) (GSM/GPRS only) |  |  | enum
00083 | [W] | SetRtcMinute | Set Real Time Clock (Minutes) (GSM/GPRS only) |  |  | enum
00084 | [W] | SetRtcHour | Set Real Time Clock (Hours) (GSM/GPRS only) |  |  | enum
00085 | [W] | SetRtcDay | Set Real Time Clock (Day) (GSM/GPRS only) |  |  | enum
00086 | [W] | SetRtcMonth | Set Real Time Clock (Month) (GSM/GPRS only) |  |  | enum
00087 | [W] | SetRtcYear | Set Real Time Clock (Year - after 2000) (GSM/GPRS only) |  |  | enum
00088.0 | [W] | SetRtc | Set Real Time Clock (Normal format) (GSM/GPRS only) | 0 = No command 1 = Set the clock |  | bool
00089 | [R] | Status.UNIXRealTimeClockHI | Real Time Clock (32 bit UNIX format) (GSM/GPRS only) |  | 1 | s
00090 | [R] | Status.UNIXRealTimeClockLO
00091 | [R] | Status.RtcSecond | Real time clock - Seconds (GSM/GPRS only) |  |  | enum
00092 | [R] | Status.RtcMinute | Real time clock - Minutes (GSM/GPRS only) |  |  | enum
00093 | [R] | Status.RtcHour | Real time clock - Hours (GSM/GPRS only) |  |  | enum
00094 | [R] | Status.RtcDay | Real time clock - Day of month (GSM/GPRS only) |  |  | enum
00095 | [R] | Status.RtcMonth | Real time clock - Month (GSM/GPRS only) |  |  | enum
00096 | [R] | Status.RtcYear | Real time clock - Year (after 2000) (GSM/GPRS only) |  |  | enum
00097.0 | [R] | Status.AcknowledgeSetRTC | Acknowledge of Set Real Time Clock command (GSM/GPRS only) | 0 = No acknowledge 1 = Acknowledged |  | bool
CONTROL AND SETTINGS [W]
00101.0 | [W] | ResetFault | Reset alarms/warnings | 0 = No resetting 1 = Reset alarm |  | bool
00101.1 | [W] | ResetHistory | Reset history | 0 = No resetting 1 = Reset history |  | bool
00101.2 | [W] | PitPump1ResetHistory | Reset history for pump 1 | 0 = No resetting 1 = Reset history |  | bool
00101.3 | [W] | PitPump2ResetHistory | Reset history for pump 2 | 0 = No resetting 1 = Reset history |  | bool
00101.4 | [W] | PitPump3ResetHistory | Reset history for pump 3 | 0 = No resetting 1 = Reset history |  | bool
00101.5 | [W] | PitPump4ResetHistory | Reset history for pump 4 | 0 = No resetting 1 = Reset history |  | bool
00101.6 | [W] | PitPump1ResetFault | Reset alarm/warning on pump 1 | 0 = No resetting 1 = Reset alarm |  | bool
00101.7 | [W] | PitPump2ResetFault | Reset alarm/warning on pump 2 | 0 = No resetting 1 = Reset alarm |  | bool
00101.8 | [W] | PitPump3ResetFault | Reset alarm/warning on pump 3 | 0 = No resetting 1 = Reset alarm |  | bool
00101.9 | [W] | PitPump4ResetFault | Reset alarm/warning on pump 4 | 0 = No resetting 1 = Reset alarm |  | bool
00101.10 | [W] | PitPump1PumpDown | Pump-down pump 1 | 0 = No command 1 = Pump down |  | bool
00101.11 | [W] | PitPump2PumpDown | Pump-down pump 2 | 0 = No command 1 = Pump down |  | bool
00101.12 | [W] | PitPump3PumpDown | Pump-down pump 3 | 0 = No command 1 = Pump down |  | bool
00101.13 | [W] | PitPump4PumpDown | Pump-down pump 4 | 0 = No command 1 = Pump down |  | bool
00102 | [W] | SetSinglePitStopLevel | Setting of pit stop level |  | 0.01 | m
00103 | [W] | SetSinglePitStartLevelMax | Setting of pit max start level |  | 0.01 | m
00104 | [W] | SetSinglePitStartLevelBand | Setting of pit start level band |  | 0.01 | m
00105 | [W] | SetSinglePitHighWaterLevel | Setting of pit high water level setting |  | 0.01 | m
00106 | [W] | SetMultiPitPump1StopLevel | Setting of pump 1 stop level |  | 0.01 | m
00107 | [W] | SetMultiPitPump1StartLevelMax | Setting of pump 1 max start level |  | 0.01 | m
00108 | [W] | SetMultiPitPump1StartLevelBand | Setting of pump 1 start level band |  | 0.01 | m
00109 | [W] | SetMultiPitPump1HighWaterLevel | Setting of pump 1 high water level setting |  | 0.01 | m
00110 | [W] | SetMultiPitPump2StopLevel | Setting of pump 2 stop level |  | 0.01 | m
00111 | [W] | SetMultiPitPump2StartLevelMax | Setting of pump 2 max start level |  | 0.01 | m
00112 | [W] | SetMultiPitPump2StartLevelBand | Setting of pump 2 start level band |  | 0.01 | m
00113 | [W] | SetMultiPitPump2HighWaterLevel | Setting of pump 2 high water level setting |  | 0.01 | m
00114 | [W] | SetMultiPitPump3StopLevel | Setting of pump 3 stop level |  | 0.01 | m
00115 | [W] | SetMultiPitPump3StartLevelMax | Setting of pump 3 max start level |  | 0.01 | m
00116 | [W] | SetMultiPitPump3StartLevelBand | Setting of pump 3 start level band |  | 0.01 | m
00117 | [W] | SetMultiPitPump3HighWaterLevel | Setting of pump 3 high water level setting |  | 0.01 | m
00118 | [W] | SetMultiPitPump4StopLevel | Setting of pump 4 stop level |  | 0.01 | m
00119 | [W] | SetMultiPitPump4StartLevelMax | Setting of pump 4 max start level |  | 0.01 | m
00120 | [W] | SetMultiPitPump4StartLevelBand | Setting of pump 4 start level band |  | 0.01 | m
00121 | [W] | SetMultiPitPump4HighWaterLevel | Setting of pump 4 high water level setting |  | 0.01 | m
00122 | [W] | PitPump1Control | Remote manual control of pump 1 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00123 | [W] | PitPump2Control | Remote manual control of pump 2 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00124 | [W] | PitPump3Control | Remote manual control of pump 3 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00125 | [W] | PitPump4Control | Remote manual control of pump 4 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
STATUS [R]
00201.0 | [R] | ResetFaultAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.1 | [R] | ResetHistoryAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.2 | [R] | PitPump1ResetHistoryAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.3 | [R] | PitPump2ResetHistoryAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.4 | [R] | PitPump3ResetHistoryAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.5 | [R] | PitPump4ResetHistoryAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.6 | [R] | PitPump1ResetFaultAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.7 | [R] | PitPump2ResetFaultAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.8 | [R] | PitPump3ResetFaultAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.9 | [R] | PitPump4ResetFaultAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.10 | [R] | PitPump1PumpDownAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.11 | [R] | PitPump2PumpDownAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.12 | [R] | PitPump3PumpDownAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.13 | [R] | PitPump4PumpDownAck | Acknowledge bit | 0 = No acknowledge 1 = Acknowledged |  | bool
00202.0 | [R] | Alarm | Actual alarm condition | 0 = No active alarms 1 = One or more active alarms |  | bool
00202.1 | [R] | Warning | Actual warning condition. | 0 = No active warnings 1 = One or more active warnings |  | bool
00202.2 | [R] | ManualControl | Manual control condition. | 0 = Auto 1 = Manual (Forced Start/Stop/Pump-down) |  | bool
00203 | [R] | PitMode | Actual mode of the pit. | 0 = Single pit mode 1 = Multi pit mode |  | enum
00204 | [R] | SinglePitStopLevel | Actual stop level |  | 0.01 | m
00205 | [R] | SinglePitStartLevelMax | Actual start level maximum |  | 0.01 | m
00206 | [R] | SinglePitStartLevelBand | Actual start level band |  | 0.01 | m
00207 | [R] | SinglePitHighWaterLevel | Actual high water level |  | 0.01 | m
00208 | [R] | MultiPitPump1StopLevel | Actual stop level for pump 1 |  | 0.01 | m
00209 | [R] | MultiPitPump1StartLevelMax | Actual start level max for pump 1 |  | 0.01 | m
00210 | [R] | MultiPitPump1StartLevelBand | Actual start level band for pump 1 |  | 0.01 | m
00211 | [R] | MultiPitPump1HighWaterLevel | Actual high water level for pump 1 |  | 0.01 | m
00212 | [R] | MultiPitPump2StopLevel | Actual stop level for pump 2 |  | 0.01 | m
00213 | [R] | MultiPitPump2StartLevelMax | Actual start level max for pump 2 |  | 0.01 | m
00214 | [R] | MultiPitPump2StartLevelBand | Actual start level band for pump 2 |  | 0.01 | m
00215 | [R] | MultiPitPump2HighWaterLevel | Actual high water level for pump 2 |  | 0.01 | m
00216 | [R] | MultiPitPump3StopLevel | Actual stop level for pump 3 |  | 0.01 | m
00217 | [R] | MultiPitPump3StartLevelMax | Actual start level max for pump 3 |  | 0.01 | m
00218 | [R] | MultiPitPump3StartLevelBand | Actual start level band for pump 3 |  | 0.01 | m
00219 | [R] | MultiPitPump3HighWaterLevel | Actual high water level for pump 3 |  | 0.01 | m
00220 | [R] | MultiPitPump4StopLevel | Actual stop level for pump 4 |  | 0.01 | m
00221 | [R] | MultiPitPump4StartLevelMax | Actual start level max for pump 4 |  | 0.01 | m
00222 | [R] | MultiPitPump4StartLevelBand | Actual start level band for pump 4 |  | 0.01 | m
00223 | [R] | MultiPitPump4HighWaterLevel | Actual high water level for pump 4 |  | 0.01 | m
00224 | [R] | PitPump1OperationMode | Actual operating mode of pump 1 | 0 = Auto 1 = Started 2 = Stopped 255 = - |  | enum
00225 | [R] | PitPump2OperationMode | Actual operating mode of pump 2 | 0 = Auto 1 = Started 2 = Stopped 255 = - |  | enum
00226 | [R] | PitPump3OperationMode | Actual operating mode of pump 3 | 0 = Auto 1 = Started 2 = Stopped |  | enum
00227 | [R] | PitPump4OperationMode | Actual operating mode of pump 4 | 0 = Auto 1 = Started 2 = Stopped 255 = - |  | enum
00228 | [R] | FaultCode | A Grundfos-specific alarm code |  |  | enum
00229 | [R] | WarningCode | A Grundfos-specific warning code |  |  | enum
00230.0 | [R] | Subpump1Present | Presence of subpump 1 | 0 = Not present 1 = Present |  | bool
00230.1 | [R] | Subpump2Present | Presence of subpump 2 | 0 = Not present 1 = Present |  | bool
00230.2 | [R] | Subpump3Present | Presence of subpump 3 | 0 = Not present 1 = Present |  | bool
00230.3 | [R] | Subpump4Present | Presence of subpump 4 | 0 = Not present 1 = Present |  | bool
00231.0 | [R] | Subpump1Running | Actual running state of pump 1 | 0 = Not running 1 = Running |  | bool
00231.1 | [R] | Subpump2Running | Actual running state of pump 2 | 1 = Not running 1 = Running |  | bool
00231.2 | [R] | Subpump3Running | Actual running state of pump 3 | 2 = Not running 1 = Running |  | bool
00231.3 | [R] | Subpump4Running | Actual running state of pump 4 | 3 = Not running 1 = Running |  | bool
00232.0 | [R] | Subpump1Fault | Alarm state of pump 1 | 0 = No alarm 1 = Alarm |  | bool
00232.1 | [R] | Subpump2Fault | Alarm state of pump 2 | 0 = No alarm 1 = Alarm |  | bool
00232.2 | [R] | Subpump3Fault | Alarm state of pump 3 | 0 = No alarm 1 = Alarm |  | bool
00232.3 | [R] | Subpump4Fault | Alarm state of pump 4 | 0 = No alarm 1 = Alarm |  | bool
00233.0 | [R] | Subpump1CommFault | Communication status with pump 1 | 0 = Communication OK (or pump not present) 1 = Communication fault |  | bool
00233.1 | [R] | Subpump2CommFault | Communication status with pump 2 | 0 = Communication OK (or pump not present) 1 = Communication fault |  | bool
00233.2 | [R] | Subpump3CommFault | Communication status with pump 3 | 0 = Communication OK (or pump not present) 1 = Communication fault |  | bool
00233.3 | [R] | Subpump4CommFault | Communication status with pump 4 | 0 = Communication OK (or pump not present) 1 = Communication fault |  | bool
00234 | [R] | OperatingMode | Mode of operation for the pump pit | 0 = Standby 1 = Start-up delay 2 = Pumping (Level control) 5 = Stopped (Level control) 9 = Manuel control (all enabled pumps in manual control) 11 = Mains failure 13 = All enabled pumps in alarm 14 = All pumps out of operation 255 = Not available |  | enum
00235.0 | [R] | WarningInPumpOrPit | Warning in pit or pump status | 0 = No warning 1 = Warning |  | bool
00235.1 | [R] | AlarmInPumpOrPit | Alarm in pit or pump status | 0 = No alarm 1 = Alarm |  | bool
00235.2 | [R] | RESERVED | Reserved bit |  |  | bool
00235.3 | [R] | ManualControlStatus | Manual or auto control | 0 = No manual pump control activated 1 = Manual pump control activated |  | bool
00236 | [R] | GSMSignalLevelActual | Actual GSM signal level (CIM 250 only) |  | 1 | %
00237 | [R] | GSMSignalLevelAverage | Average GSM signal level (CIM 250 only) |  | 1 | %
00238 | [R] | IPAddressHI | IP Address |  |  | IP
00239 | [R] | IPAddressLO |  |  |  | IP
00240.0 | [R] | AlarmBits.ExternalFault | External fault signal | 0 = No alarm 1 = Alarm |  | bool
00240.1 | [R] | AlarmBits.CommunicationFault | Communication fault, pump | 0 = No alarm 1 = Alarm |  | bool
00240.2 | [R] | AlarmBits.Bit2 | - | 0 = No alarm 1 = Alarm |  | bool
00240.3 | [R] | AlarmBits.Pump1Fault | Pump 1 in alarm | 0 = No alarm 1 = Alarm |  | bool
00240.4 | [R] | AlarmBits.Pump2Fault | Pump 2 in alarm | 0 = No alarm 1 = Alarm |  | bool
00240.5 | [R] | AlarmBits.Pump3Fault | Pump 3 in alarm | 0 = No alarm 1 = Alarm |  | bool
00240.6 | [R] | AlarmBits.Pump4Fault | Pump 4 in alarm | 0 = No alarm 1 = Alarm |  | bool
00240.7 | [R] | AlarmBits.SensorLimit2Exceeded | Sensor limit 2 exceeded (High level) | 0 = No alarm 1 = Alarm |  | bool
00240.8 | [R] | AlarmBits.SetupConflict | Setup conflict | 0 = No alarm 1 = Alarm |  | bool
00241.0 | [R] | WarningBits.Bit0 | - | 0 = No alarm 1 = Alarm |  | bool
00241.1 | [R] | WarningBits.CommunicationFault | Communication fault, pump | 0 = No warning 1 = Warning |  | bool
00241.2 | [R] | WarningBits.VerificationError | Verification error, code area (ROM, FLASH) | 0 = No warning 1 = Warning |  | bool
00241.3 | [R] | WarningBits.Bit3 | Pump 1 has a warning | 0 = No warning 1 = Warning |  | bool
00241.4 | [R] | WarningBits.Bit4 | Pump 2 has a warning | 0 = No warning 1 = Warning |  | bool
00241.5 | [R] | WarningBits.Bit5 | Pump 3 has a warning | 0 = No warning 1 = Warning |  | bool
00241.6 | [R] | WarningBits.Bit6 | Pump 4 has a warning | 0 = No warning 1 = Warning |  | bool
00241.7 | [R] | WarningBits.Bit7 | - | 0 = No warning 1 = Warning |  | bool
00241.8 | [R] | WarningBits.SetupConflict | Setup conflict | 0 = No warning 1 = Warning |  | bool
PIT DATA [R]
00301 | [R] | WaterLevel | Average of the pit water level as estimated by the pumps |  | 0.01 | m
00302 | [R] | MaxWaterLevel | Maximum value the pit water level has had. |  | 0.01 | m
00303 | [R] | Power HI | Pit power consumption |  | 1 | W
00304 | [R] | Power LO
00305 | [R] | EnergyTripCnt HI | Pit energy consumption |  | 1 | 1kWh
00306 | [R] | EnergyTripCnt LO
00307 | [R] | OnTimeCnt HI | Power on time for CIU |  | 1 | min
00308 | [R] | OnTimeCnt LO
00309 | [R] | OprTimeTripCnt HI | Pit operating time where one or more pumps has been operating |  | 1 | min
00310 | [R] | OprTimeTripCnt LO
00311 | [R] | PumpOperationTimePct | Time percentage for the last 30 days where one or more pumps has been operating |  | 0.01 | %
00312 | [R] | MultiPumpOperationTimePct | Percentage of the operating time for the last 30 days where more than one pump is operating. |  | 0.01 | %
00313 | [R] | MultiPumpOperationTimeMax | Logged value of max time within the last 30 days where more than one pump has been operating continuously. |  | 1 | s
00314 | [R] | DigitalInput | Digital inputs (bitscaled) |  |  | unscaled
SUBPUMP DATA [R]
00401 | [R] | SubPump1.MotorTemperature | Motor temperature, pump 1 |  | 0.01 | K
00402 | [R] | SubPump1.ElectronicTemperature | Electronics temperature, pump 1 |  | 0.01 | K
00403 | [R] | SubPump1.AverageLineVoltage | Average pump line voltage, pump 1 |  | 0.1 | V
00404 | [R] | SubPump1.AverageLineCurrent | Average pump line current, pump 1 |  | 0.1 | A
00405 | [R] | SubPump1.AverageLineCurrentLatest | Average pump line current the last time it was running, pump 1 |  | 0.1 | A
00406 | [R] | SubPump1.LineFrequency | Line frequency of pump power supply, pump 1 |  | 0.1 | Hz
00407 | [R] | SubPump1.PhaseSequence | Phase sequence of pump power supply, pump 1 |  |  | unscaled
00408 | [R] | SubPump1.CosPhi | Power factor, pump 1 |  | 0.01 | -
00409 | [R] | SubPump1.Power | Power consumption, pump 1 |  | 1 | W
00410 | [R] | SubPump1.EnergyTripCounter HI | Energy consumption, pump 1 |  | 1 | kWh
00411 | [R] | SubPump1.EnergyTripCounter LO
00412 | [R] | SubPump1.WaterLevel | Water level as estimated by the pump 1 |  | 0.01 | m
00413 | [R] | SubPump1.WaterLevelMax | Logged max value of water level by pump 1 |  | 0.01 | m
00414 | [R] | SubPump1.MaxContinousTime | Logged max value of continuous opr. time the last 30 days, pump 1. |  | 1 | min
00415 | [R] | SubPump1.TotalPoweredTime HI | The total time pump 1 has been powered on |  | 1 | min
00416 | [R] | SubPump1.TotalPoweredTime LO
00417 | [R] | SubPump1.OperationTime HI | The total time pump 1 has been operating |  | 1 | min
00418 | [R] | SubPump1.OperationTime LO
00419 | [R] | SubPump1.OperationTimeTripCounter HI | Trip counter of the total time pump 1 has been operating |  | 1 | min
00420 | [R] | SubPump1.OperationTimeTripCounter LO
00421 | [R] | SubPump1.NumberOfStarts HI | The total number of starts of pump 1 |  |  | unscaled
00422 | [R] | SubPump1.NumberOfStarts LO
00423 | [R] | SubPump1.NumberOfStartsTripCounter HI | Trip counter of the total number of starts of pump 1. |  |  | unscaled
00424 | [R] | SubPump1.NumberOfStartsTripCounter LO
00425 | [R] | SubPump1.AlarmCode | Pump 1 Grundfos-specific alarm code. |  |  | unscaled
00426 | [R] | SubPump1.WarningCode | Pump 1 Grundfos-specific warning code. |  |  | unscaled
00427 | [R] | SubPump1.OperatingMode | Actual operating mode of pump 1 | 0 = Auto (Power on default) 1 = Start, forced to be started 2 = Stop, forced to be stopped 255 = - |  | enum
00428.0 | [R] | Subpump1Alarms.PhaseSequence | Phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00428.1 | [R] | Subpump1Alarms.Overvoltage | Overvoltage | 0 = No alarm 1 = Alarm |  | bool
00428.2 | [R] | Subpump1Alarms.Undervoltage | Undervoltage | 0 = No alarm 1 = Alarm |  | bool
00428.3 | [R] | Subpump1Alarms.Overload | Overload | 0 = No alarm 1 = Alarm |  | bool
00428.4 | [R] | Subpump1Alarms.BlockedMotor | Blocked motor/pump | 0 = No alarm 1 = Alarm |  | bool
00428.5 | [R] | Subpump1Alarms.AlarmBit5 | - | 0 = No alarm 1 = Alarm |  | bool
00428.6 | [R] | Subpump1Alarms.MotorTemperature | Motor Temperature | 0 = No alarm 1 = Alarm |  | bool
00428.7 | [R] | Subpump1Alarms.ElectronicTemperature | Temperature, control electronics | 0 = No alarm 1 = Alarm |  | bool
00428.8 | [R] | Subpump1Alarms.TermoRelay1 | Termo Relay 1 in motor (e.g. Clixon) | 0 = No alarm 1 = Alarm |  | bool
00428.9 | [R] | Subpump1Alarms.TermoRelay2 | Termo Relay 2 in motor (e.g. termistor) | 0 = No alarm 1 = Alarm |  | bool
00428.10 | [R] | Subpump1Alarms.VerificationError | Verification error, code area (ROM, FLASH) | 0 = No alarm 1 = Alarm |  | bool
00428.11 | [R] | Subpump1Alarms.AlarmBit11 | - | 0 = No alarm 1 = Alarm |  | bool
00428.12 | [R] | Subpump1Alarms.SensorFault | Sensor Fault | 0 = No alarm 1 = Alarm |  | bool
00428.13 | [R] | Subpump1Alarms.AlarmBit13 | - | 0 = No alarm 1 = Alarm |  | bool
00429.0 | [R] | Subpump1Warnings.WarningBit0 | - | 0 = No warning 1 = Warning |  | bool
00429.1 | [R] | Subpump1Warnings.WarningBit1 | - | 0 = No warning 1 = Warning |  | bool
00429.2 | [R] | Subpump1Warnings.WarningBit2 | - | 0 = No warning 1 = Warning |  | bool
00429.3 | [R] | Subpump1Warnings.Overload | Overload | 0 = No warning 1 = Warning |  | bool
00429.4 | [R] | Subpump1Warnings.WarningBit4 | - | 0 = No warning 1 = Warning |  | bool
00429.5 | [R] | Subpump1Warnings.DryRunning | Dry Running | 0 = No warning 1 = Warning |  | bool
00429.6 | [R] | Subpump1Warnings.MotorTemperature | Motor Temperature | 0 = No warning 1 = Warning |  | bool
00429.7 | [R] | Subpump1Warnings.ElectronicTemperature | Temperature, control electronics | 0 = No warning 1 = Warning |  | bool
00429.8 | [R] | Subpump1Warnings.WarningBit8 | - | 0 = No warning 1 = Warning |  | bool
00429.9 | [R] | Subpump1Warnings.WarningBit9 | - | 0 = No warning 1 = Warning |  | bool
00429.10 | [R] | Subpump1Warnings.VerificationError | Verification error, code area (ROM, FLASH) | 0 = No warning 1 = Warning |  | bool
00429.11 | [R] | Subpump1Warnings.VerificationErrorEEPROM | Verification error, FE parameter area (EEPROM) | 0 = No warning 1 = Warning |  | bool
00429.12 | [R] | Subpump1Warnings.SensorFault | Sensor Fault | 0 = No warning 1 = Warning |  | bool
00429.13 | [R] | Subpump1Warnings.SensorLimitExceeded | Sensor limit 2 exceeded (High level) | 0 = No warning 1 = Warning |  | bool
00451 | [R] | SubPump2.MotorTemperature | Motor temperature, pump 2 |  | 0.01 | K
00452 | [R] | SubPump2.ElectronicTemperature | Electronics temperature, pump 2 |  | 0.01 | K
00453 | [R] | SubPump2.AverageLineVoltage | Average pump line voltage, pump 2 |  | 0.1 | V
00454 | [R] | SubPump2.AverageLineCurrent | Average pump line current, pump 2 |  | 0.1 | A
00455 | [R] | SubPump2.AverageLineCurrentLatest | Average pump line current the last time it was running, pump 2 |  | 0.1 | A
00456 | [R] | SubPump2.LineFrequency | Line frequency of pump power supply, pump 2 |  | 0.1 | Hz
00457 | [R] | SubPump2.PhaseSequence | Phase sequence of pump power supply, pump 2 |  |  | unscaled
00458 | [R] | SubPump2.CosPhi | Power factor, pump 2 |  | 0.01 | -
00459 | [R] | SubPump2.Power | Power consumption, pump 2 |  | 1 | W
00460 | [R] | SubPump2.EnergyTripCounter HI | Energy consumption, pump 2 |  | 1 | kWh
00461 | [R] | SubPump2.EnergyTripCounter LO
00462 | [R] | SubPump2.WaterLevel | Water level as estimated by the pump 2 |  | 0.01 | m
00463 | [R] | SubPump2.WaterLevelMax | Logged max value of water level by pump 2 |  | 0.01 | m
00464 | [R] | SubPump2.MaxContinousTime | Logged max value of continuous opr. time the last 30 days, pump 2. |  | 1 | min
00465 | [R] | SubPump2.TotalPoweredTime HI | The total time pump 2 has been powered on |  | 1 | min
00466 | [R] | SubPump2.TotalPoweredTime LO
00467 | [R] | SubPump2.OperationTime HI | The total time pump 2 has been operating |  | 1 | min
00468 | [R] | SubPump2.OperationTime LO
00469 | [R] | SubPump2.OperationTimeTripCounter HI | Trip counter of the total time pump 2 has been operating |  | 1 | min
00470 | [R] | SubPump2.OperationTimeTripCounter LO
00471 | [R] | SubPump2.NumberOfStarts HI | The total number of starts of pump 2 |  |  | unscaled
00472 | [R] | SubPump2.NumberOfStarts LO
00473 | [R] | SubPump2.NumberOfStartsTripCounter HI | Trip counter of the total number of starts of pump 2. |  |  | unscaled
00474 | [R] | SubPump2.NumberOfStartsTripCounter LO
00475 | [R] | SubPump2.AlarmCode | Pump 2 Grundfos-specific alarm code. |  |  | unscaled
00476 | [R] | SubPump2.WarningCode | Pump 2 Grundfos-specific warning code. |  |  | unscaled
00477 | [R] | SubPump2.OperatingMode | Actual operating mode of pump 2 | 0 = Auto (Power on default) 1 = Start, forced to be started 2 = Stop, forced to be stopped 255 = - |  | enum
00478.0 | [R] | Subpump2Alarms.PhaseSequence | Phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00478.1 | [R] | Subpump2Alarms.Overvoltage | Overvoltage | 0 = No alarm 1 = Alarm |  | bool
00478.2 | [R] | Subpump2Alarms.Undervoltage | Undervoltage | 0 = No alarm 1 = Alarm |  | bool
00478.3 | [R] | Subpump2Alarms.Overload | Overload | 0 = No alarm 1 = Alarm |  | bool
00478.4 | [R] | Subpump2Alarms.BlockedMotor | Blocked motor/pump | 0 = No alarm 1 = Alarm |  | bool
00478.5 | [R] | Subpump2Alarms.AlarmBit5 | - | 0 = No alarm 1 = Alarm |  | bool
00478.6 | [R] | Subpump2Alarms.MotorTemperature | Motor Temperature | 0 = No alarm 1 = Alarm |  | bool
00478.7 | [R] | Subpump2Alarms.ElectronicTemperature | Temperature, control electronics | 0 = No alarm 1 = Alarm |  | bool
00478.8 | [R] | Subpump2Alarms.TermoRelay1 | Termo Relay 1 in motor (e.g. Clixon) | 0 = No alarm 1 = Alarm |  | bool
00478.9 | [R] | Subpump2Alarms.TermoRelay2 | Termo Relay 2 in motor (e.g. termistor) | 0 = No alarm 1 = Alarm |  | bool
00478.10 | [R] | Subpump2Alarms.VerificationError | Verification error, code area (ROM, FLASH) | 0 = No alarm 1 = Alarm |  | bool
00478.11 | [R] | Subpump2Alarms.AlarmBit11 | - | 0 = No alarm 1 = Alarm |  | bool
00478.12 | [R] | Subpump2Alarms.SensorFault | Sensor Fault | 0 = No alarm 1 = Alarm |  | bool
00478.13 | [R] | Subpump2Alarms.AlarmBit13 | - | 0 = No alarm 1 = Alarm |  | bool
00479.0 | [R] | Subpump2Warnings.WarningBit0 | - | 0 = No warning 1 = Warning |  | bool
00479.1 | [R] | Subpump2Warnings.WarningBit1 | - | 0 = No warning 1 = Warning |  | bool
00479.2 | [R] | Subpump2Warnings.WarningBit2 | - | 0 = No warning 1 = Warning |  | bool
00479.3 | [R] | Subpump2Warnings.Overload | Overload | 0 = No warning 1 = Warning |  | bool
00479.4 | [R] | Subpump2Warnings.WarningBit4 | - | 0 = No warning 1 = Warning |  | bool
00479.5 | [R] | Subpump2Warnings.DryRunning | Dry Running | 0 = No warning 1 = Warning |  | bool
00479.6 | [R] | Subpump2Warnings.MotorTemperature | Motor Temperature | 0 = No warning 1 = Warning |  | bool
00479.7 | [R] | Subpump2Warnings.ElectronicTemperature | Temperature, control electronics | 0 = No warning 1 = Warning |  | bool
00479.8 | [R] | Subpump2Warnings.WarningBit8 | - | 0 = No warning 1 = Warning |  | bool
00479.9 | [R] | Subpump2Warnings.WarningBit9 | - | 0 = No warning 1 = Warning |  | bool
00479.10 | [R] | Subpump2Warnings.VerificationError | Verification error, code area (ROM, FLASH) | 0 = No warning 1 = Warning |  | bool
00479.11 | [R] | Subpump2Warnings.VerificationErrorEEPROM | Verification error, FE parameter area (EEPROM) | 0 = No warning 1 = Warning |  | bool
00479.12 | [R] | Subpump2Warnings.SensorFault | Sensor Fault | 0 = No warning 1 = Warning |  | bool
00479.13 | [R] | Subpump2Warnings.SensorLimitExceeded | Sensor limit 2 exceeded (High level) | 0 = No warning 1 = Warning |  | bool
00501 | [R] | SubPump3.MotorTemperature | Motor temperature, pump 3 |  | 0.01 | K
00502 | [R] | SubPump3.ElectronicTemperature | Electronics temperature, pump 3 |  | 0.01 | K
00503 | [R] | SubPump3.AverageLineVoltage | Average pump line voltage, pump 3 |  | 0.1 | V
00504 | [R] | SubPump3.AverageLineCurrent | Average pump line current, pump 3 |  | 0.1 | A
00505 | [R] | SubPump3.AverageLineCurrentLatest | Average pump line current the last time it was running, pump 3 |  | 0.1 | A
00506 | [R] | SubPump3.LineFrequency | Line frequency of pump power supply, pump 3 |  | 0.1 | Hz
00507 | [R] | SubPump3.PhaseSequence | Phase sequence of pump power supply, pump 3 |  |  | unscaled
00508 | [R] | SubPump3.CosPhi | Power factor, pump 3 |  | 0.01 | -
00509 | [R] | SubPump3.Power | Power consumption, pump 3 |  | 1 | W
00510 | [R] | SubPump3.EnergyTripCounter HI | Energy consumption, pump 3 |  | 1 | kWh
00511 | [R] | SubPump3.EnergyTripCounter LO
00512 | [R] | SubPump3.WaterLevel | Water level as estimated by the pump 3 |  | 0.01 | m
00513 | [R] | SubPump3.WaterLevelMax | Logged max value of water level by pump 3 |  | 0.01 | m
00514 | [R] | SubPump3.MaxContinousTime | Logged max value of continuous opr. time the last 30 days, pump 3. |  | 1 | min
00515 | [R] | SubPump3.TotalPoweredTime HI | The total time pump 3 has been powered on |  | 1 | min
00516 | [R] | SubPump3.TotalPoweredTime LO
00517 | [R] | SubPump3.OperationTime HI | The total time pump 3 has been operating |  | 1 | min
00518 | [R] | SubPump3.OperationTime LO
00519 | [R] | SubPump3.OperationTimeTripCounter HI | Trip counter of the total time pump 3 has been operating |  | 1 | min
00520 | [R] | SubPump3.OperationTimeTripCounter LO
00521 | [R] | SubPump3.NumberOfStarts HI | The total number of starts of pump 3 |  |  | unscaled
00522 | [R] | SubPump3.NumberOfStarts LO
00523 | [R] | SubPump3.NumberOfStartsTripCounter HI | Trip counter of the total number of starts of pump 3. |  |  | unscaled
00524 | [R] | SubPump3.NumberOfStartsTripCounter LO
00525 | [R] | SubPump3.AlarmCode | Pump 3 Grundfos-specific alarm code. |  |  | unscaled
00526 | [R] | SubPump3.WarningCode | Pump 3 Grundfos-specific warning code. |  |  | unscaled
00527 | [R] | SubPump3.OperatingMode | Actual operating mode of pump 3 | 0 = Auto (Power on default) 1 = Start, forced to be started 2 = Stop, forced to be stopped 255 = - |  | enum
00528.0 | [R] | Subpump3Alarms.PhaseSequence | Phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00528.1 | [R] | Subpump3Alarms.Overvoltage | Overvoltage | 0 = No alarm 1 = Alarm |  | bool
00528.2 | [R] | Subpump3Alarms.Undervoltage | Undervoltage | 0 = No alarm 1 = Alarm |  | bool
00528.3 | [R] | Subpump3Alarms.Overload | Overload | 0 = No alarm 1 = Alarm |  | bool
00528.4 | [R] | Subpump3Alarms.BlockedMotor | Blocked motor/pump | 0 = No alarm 1 = Alarm |  | bool
00528.5 | [R] | Subpump3Alarms.AlarmBit5 | - | 0 = No alarm 1 = Alarm |  | bool
00528.6 | [R] | Subpump3Alarms.MotorTemperature | Motor Temperature | 0 = No alarm 1 = Alarm |  | bool
00528.7 | [R] | Subpump3Alarms.ElectronicTemperature | Temperature, control electronics | 0 = No alarm 1 = Alarm |  | bool
00528.8 | [R] | Subpump3Alarms.TermoRelay1 | Termo Relay 1 in motor (e.g. Clixon) | 0 = No alarm 1 = Alarm |  | bool
00528.9 | [R] | Subpump3Alarms.TermoRelay2 | Termo Relay 2 in motor (e.g. termistor) | 0 = No alarm 1 = Alarm |  | bool
00528.10 | [R] | Subpump3Alarms.VerificationError | Verification error, code area (ROM, FLASH) | 0 = No alarm 1 = Alarm |  | bool
00528.11 | [R] | Subpump3Alarms.AlarmBit11 | - | 0 = No alarm 1 = Alarm |  | bool
00528.12 | [R] | Subpump3Alarms.SensorFault | Sensor Fault | 0 = No alarm 1 = Alarm |  | bool
00528.13 | [R] | Subpump3Alarms.AlarmBit13 | - | 0 = No alarm 1 = Alarm |  | bool
00529.0 | [R] | Subpump3Warnings.WarningBit0 | - | 0 = No warning 1 = Warning |  | bool
00529.1 | [R] | Subpump3Warnings.WarningBit1 | - | 0 = No warning 1 = Warning |  | bool
00529.2 | [R] | Subpump3Warnings.WarningBit2 | - | 0 = No warning 1 = Warning |  | bool
00529.3 | [R] | Subpump3Warnings.Overload | Overload | 0 = No warning 1 = Warning |  | bool
00529.4 | [R] | Subpump3Warnings.WarningBit4 | - | 0 = No warning 1 = Warning |  | bool
00529.5 | [R] | Subpump3Warnings.DryRunning | Dry Running | 0 = No warning 1 = Warning |  | bool
00529.6 | [R] | Subpump3Warnings.MotorTemperature | Motor Temperature | 0 = No warning 1 = Warning |  | bool
00529.7 | [R] | Subpump3Warnings.ElectronicTemperature | Temperature, control electronics | 0 = No warning 1 = Warning |  | bool
00529.8 | [R] | Subpump3Warnings.WarningBit8 | - | 0 = No warning 1 = Warning |  | bool
00529.9 | [R] | Subpump3Warnings.WarningBit9 | - | 0 = No warning 1 = Warning |  | bool
00529.10 | [R] | Subpump3Warnings.VerificationError | Verification error, code area (ROM, FLASH) | 0 = No warning 1 = Warning |  | bool
00529.11 | [R] | Subpump3Warnings.VerificationErrorEEPROM | Verification error, FE parameter area (EEPROM) | 0 = No warning 1 = Warning |  | bool
00529.12 | [R] | Subpump3Warnings.SensorFault | Sensor Fault | 0 = No warning 1 = Warning |  | bool
00529.13 | [R] | Subpump3Warnings.SensorLimitExceeded | Sensor limit 2 exceeded (High level) | 0 = No warning 1 = Warning |  | bool
00551 | [R] | SubPump4.MotorTemperature | Motor temperature, pump 4 |  | 0.01 | K
00552 | [R] | SubPump4.ElectronicTemperature | Electronics temperature, pump 4 |  | 0.01 | K
00553 | [R] | SubPump4.AverageLineVoltage | Average pump line voltage, pump 4 |  | 0.1 | V
00554 | [R] | SubPump4.AverageLineCurrent | Average pump line current, pump 4 |  | 0.1 | A
00555 | [R] | SubPump4.AverageLineCurrentLatest | Average pump line current the last time it was running, pump 4 |  | 0.1 | A
00556 | [R] | SubPump4.LineFrequency | Line frequency of pump power supply, pump 4 |  | 0.1 | Hz
00557 | [R] | SubPump4.PhaseSequence | Phase sequence of pump power supply, pump 4 |  |  | unscaled
00558 | [R] | SubPump4.CosPhi | Power factor, pump 4 |  | 0.01 | -
00559 | [R] | SubPump4.Power | Power consumption, pump 4 |  | 1 | W
00560 | [R] | SubPump4.EnergyTripCounter HI | Energy consumption, pump 4 |  | 1 | kWh
00561 | [R] | SubPump4.EnergyTripCounter LO
00562 | [R] | SubPump4.WaterLevel | Water level as estimated by the pump 4 |  | 0.01 | m
00563 | [R] | SubPump4.WaterLevelMax | Logged max value of water level by pump 4 |  | 0.01 | m
00564 | [R] | SubPump4.MaxContinousTime | Logged max value of continuous opr. time the last 30 days, pump 4. |  | 1 | min
00565 | [R] | SubPump4.TotalPoweredTime HI | The total time pump 4 has been powered on |  | 1 | min
00566 | [R] | SubPump4.TotalPoweredTime LO
00567 | [R] | SubPump4.OperationTime HI | The total time pump 4 has been operating |  | 1 | min
00568 | [R] | SubPump4.OperationTime LO
00569 | [R] | SubPump4.OperationTimeTripCounter HI | Trip counter of the total time pump 4 has been operating |  | 1 | min
00570 | [R] | SubPump4.OperationTimeTripCounter LO
00571 | [R] | SubPump4.NumberOfStarts HI | The total number of starts of pump 4 |  |  | unscaled
00572 | [R] | SubPump4.NumberOfStarts LO
00573 | [R] | SubPump4.NumberOfStartsTripCounter HI | Trip counter of the total number of starts of pump 4. |  |  | unscaled
00574 | [R] | SubPump4.NumberOfStartsTripCounter LO
00575 | [R] | SubPump4.AlarmCode | Pump 4 Grundfos-specific alarm code. |  |  | unscaled
00576 | [R] | SubPump4.WarningCode | Pump 4 Grundfos-specific warning code. |  |  | unscaled
00577 | [R] | SubPump4.OperatingMode | Actual operating mode of pump 4 | 0 = Auto (Power on default) 1 = Start, forced to be started 2 = Stop, forced to be stopped 255 = - |  | enum
00578.0 | [R] | Subpump4Alarms.PhaseSequence | Phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00578.1 | [R] | Subpump4Alarms.Overvoltage | Overvoltage | 0 = No alarm 1 = Alarm |  | bool
00578.2 | [R] | Subpump4Alarms.Undervoltage | Undervoltage | 0 = No alarm 1 = Alarm |  | bool
00578.3 | [R] | Subpump4Alarms.Overload | Overload | 0 = No alarm 1 = Alarm |  | bool
00578.4 | [R] | Subpump4Alarms.BlockedMotor | Blocked motor/pump | 0 = No alarm 1 = Alarm |  | bool
00578.5 | [R] | Subpump4Alarms.AlarmBit5 | - | 0 = No alarm 1 = Alarm |  | bool
00578.6 | [R] | Subpump4Alarms.MotorTemperature | Motor Temperature | 0 = No alarm 1 = Alarm |  | bool
00578.7 | [R] | Subpump4Alarms.ElectronicTemperature | Temperature, control electronics | 0 = No alarm 1 = Alarm |  | bool
00578.8 | [R] | Subpump4Alarms.TermoRelay1 | Termo Relay 1 in motor (e.g. Clixon) | 0 = No alarm 1 = Alarm |  | bool
00578.9 | [R] | Subpump4Alarms.TermoRelay2 | Termo Relay 2 in motor (e.g. termistor) | 0 = No alarm 1 = Alarm |  | bool
00578.10 | [R] | Subpump4Alarms.VerificationError | Verification error, code area (ROM, FLASH) | 0 = No alarm 1 = Alarm |  | bool
00578.11 | [R] | Subpump4Alarms.AlarmBit11 | - | 0 = No alarm 1 = Alarm |  | bool
00578.12 | [R] | Subpump4Alarms.SensorFault | Sensor Fault | 0 = No alarm 1 = Alarm |  | bool
00578.13 | [R] | Subpump4Alarms.AlarmBit13 | - | 0 = No alarm 1 = Alarm |  | bool
00579.0 | [R] | Subpump4Warnings.WarningBit0 | - | 0 = No warning 1 = Warning |  | bool
00579.1 | [R] | Subpump4Warnings.WarningBit1 | - | 0 = No warning 1 = Warning |  | bool
00579.2 | [R] | Subpump4Warnings.WarningBit2 | - | 0 = No warning 1 = Warning |  | bool
00579.3 | [R] | Subpump4Warnings.Overload | Overload | 0 = No warning 1 = Warning |  | bool
00579.4 | [R] | Subpump4Warnings.WarningBit4 | - | 0 = No warning 1 = Warning |  | bool
00579.5 | [R] | Subpump4Warnings.DryRunning | Dry Running | 0 = No warning 1 = Warning |  | bool
00579.6 | [R] | Subpump4Warnings.MotorTemperature | Motor Temperature | 0 = No warning 1 = Warning |  | bool
00579.7 | [R] | Subpump4Warnings.ElectronicTemperature | Temperature, control electronics | 0 = No warning 1 = Warning |  | bool
00579.8 | [R] | Subpump4Warnings.WarningBit8 | - | 0 = No warning 1 = Warning |  | bool
00579.9 | [R] | Subpump4Warnings.WarningBit9 | - | 0 = No warning 1 = Warning |  | bool
00579.10 | [R] | Subpump4Warnings.VerificationError | Verification error, code area (ROM, FLASH) | 0 = No warning 1 = Warning |  | bool
00579.11 | [R] | Subpump4Warnings.VerificationErrorEEPROM | Verification error, FE parameter area (EEPROM) | 0 = No warning 1 = Warning |  | bool
00579.12 | [R] | Subpump4Warnings.SensorFault | Sensor Fault | 0 = No warning 1 = Warning |  | bool
00579.13 | [R] | Subpump4Warnings.SensorLimitExceeded | Sensor limit 2 exceeded (High level) | 0 = No warning 1 = Warning |  | bool
SIMULATION [R/W]
00701 | [W] | Simulation.AlarmCode | Alarm code to simulate. |  |  | unscaled
00702 | [W] | Simulation.WarningCode | Warning code to simulate |  |  | unscaled
00703.0 | [W] | Simulation.Activate | Activation of simulation features. | 0 = Deactivate simulation 1 = Activate simulation |  | bool
00704.0 | [R] | Simulation.Active | Event simulation status | 0 = Not active 1 = Simulation active |  | bool
USER REGISTERS [R/W]
00751 | [R/W] | UserLabel1 |  |  |  | unscaled
00752 | [R/W] | UserLabel2 |  |  |  | unscaled
00753 | [R/W] | UserLabel3 |  |  |  | unscaled
00754-00799 | [R/W] | UserLabel4...UserLabel49 |  |  |  | unscaled
00800 | [R/W] | UserLabel50 |  |  |  | unscaled

## CU 362
GRUNDFOS CIM/CIU 200/260/500 MODBUS profile for CU 362 Dedicated Controls
Sheet version: 02.10.06
Change date (d-m-y): 15-10-2018
All addresses are registers (16 bit), and the address is written in decimal format
Reg. addr. | Access | Modbus parameter name | Modbus notes | Description | Bool/Enum description | Modbus Scale | Modbus Unit
CIM CONFIG [R/W] - All saved in EEPROM
00001 | [R/W] | Config.SlaveMinimumReplyDelay | Saved in EEPROM | For adding a reply delay in ms |  | 1 | ms
00002 | [R/W] | RESERVED |  |  |  |  | unscaled
00003 | [R/W] | Config.SoftwareDefinedModbusAddress | Saved in EEPROM. If switch value is invalid, then use the value in this register as Modbus address. Make 0xE7 the default value. | Set a Modbus slave address to use if the address switches are set to an invalid value (Modbus RTU only). |  |  | unscaled
00004 | [R/W] | Config.SoftwareDefinedBitRate | Saved in EEPROM. Default = 4800. | If set to software defined, use this bit rate (Modbus RTU only). | 0 = 1200 1 = 2400 2 = 4800 3 = 9600 4 = 19200 5 = 38400 |  | enum
00005.0 | [R/W] | Config.AutoAckControlBits | Saved in EEPROM. 0 = Control bits are manually lowered. 1 = Control bits are automatically lowered, when module receives the event. (default) | Acknowlege behaviour of control bits | 0 = Manual, 1 = Automatic |  | bool
00006.0 | [R/W] | Config.ReadWriteSeparation | Saved in EEPROM. 0 = Registers are overwritten with values (default) 1 = Register readback is put into seperate registers | Separate reads from writes | 0 = No separation 1 = Separate registers |  | bool
00007 | [R/W] | Config.ScadaCallbackRegister | Register in the master used for unsolicited messages. CIM 250 SW handles EEPROM. | Register in the master used for unsolicited messages. (GSM/GRPS only) |  |  | unscaled
00008 | [R/W] | Config.NoDataActivityTimeout | The elapsed time with no data activity before the module issues a "GPRS restart". CIM 250 SW handles EEPROM. | The elapsed time with no data activity before the module issues a "GPRS restart". (GSM/GRPS only) |  | 1 | min
00009 | [R/W] | Config.SoftwareDefinedParity | Saved in EEPROM. Default value = 0. | If softwaredefined, use this parity setting (Modbus RTU only). | 0 = No parity 1 = Even parity 2 = Odd parity |  | enum
00010 | [R/W] | Config.SoftwareDefinedStopBit | Saved in EEPROM. Default value = 1. | If softwaredefined, use this stop bit setting (Modbus RTU only). | 0 = Not defined 1 = 1 stop bit 2 = 2 stop bit |  | enum
00013 | [R/W] | Config.GENIbusDiodeOff |  | Switching off the GENIbus diode (LED2) | 0=On (default) 1=Off |  | bool
CIM STATUS [R]
00021 | [R] | GENIbusCRCErrorCnt | GENIbus CRC err. | CRC error counter on the GENIbus |  |  | unscaled
00022 | [R] | GENIbusDataErrorCnt | GENIbus Data err. | Data error counter on the GENIbus |  |  | unscaled
00023 | [R] | CIM Software version number | Shows version number | Software version number |  |  | unscaled
00024 | [R] | ActualModbusAddress | Shows actual address | Actual modbus slave address (Read only) |  |  | unscaled
00025 | [R] | GENIbusTXcount HI | GENIbus TX tlg count HI | Transmit counter on GENIbus |  |  | unscaled
00026 | [R] | GENIbusTXcount LO | GENIbus TX tlg count LO
00027 | [R] | GENIbusRXcount HI | GENIbus RX tlg count HI | Receive counter on GENIbus |  |  | unscaled
00028 | [R] | GENIbusRXcount LO | GENIbus RX tlg count LO
00029.0 | [R] | ScadaPinCodeEnabled |  | Determines if the use of a Scada Pin Code is enabled | 0 = Pin code disabled 1 = Pin code enabled
00029.1 | [R] | WriteAccess |  | Determines if write (control) access is granted or not. | 0 = No write access 1 = Write access
00029.2 | [R] | LockinBlocked |  | Login blocked due to too many password attempts | 0 = No Login blocking 1 = Login blocked
00030 | [R] | Unit Family | Grundfos specific | Grundfos product family | 0 = - 1 = UPE/MAGNA pump 2 = MGE 7 = Motor Protection Unit 17 = Multi-E 21 = MPC / Multi-B 25 = CU 351 - CR Monitor 26 = CU 36x - Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller CU 2X1 48 = Level controller LC 2x1 255 = N/A |  | enum
00031 | [R] | Unit Type | Grundfos specific | Grundfos product type |  |  | unscaled
00032 | [R] | Unit Version | Grundfos specific | Grundfos product version |  |  | unscaled
00033 | [R] | BatteryState | Equal to gsm_battery_state (5, 52) | State of cellular module battery | 0 = Battery not present 1 = Battery must be replaced 2 = Battery charging 3 = Battery needs charging, but temperature too high 4 = Battery needs charging, but temperature too low 5 = Battery Low 6 = Battery OK 255 = Battery state not available |  | enum
00034 | [R] | ProductSoftwareVersionHI | From ASCII string | Product software version (BCD digit 1-4 aa.bb) |  |  | BCD number
00035 | [R] | ProductSoftwareVersionLO | From ASCII string | Product software version (BCD digit 5-8 cc.dd) |  |  | BCD number
00036 | [R] | ProductSoftwareDayMonth | From ASCII string | Product software date (BCD ddmm) |  |  | BCD number
00037 | [R] | ProductSoftwareYear | From ASCII string | Product software date (BCD yyyy) |  |  | BCD number
CONTROL AND SETTINGS [W]
00101.0 | [W] | PitControl.ResetAlarm | Rising edge | Reset Alarm | 0 = No resetting 1 = Reset alarm |  | bool
00101.2 | [W] | PitControl.ResetEventLog | Rising edge | Reset event log | 0 = No resetting 1 = Reset event log |  | bool
00101.3 | [W] | PitControl.InterlockPit | Rising edge | Interlock command | 0 = No command 1 = Interlock pit |  | bool
00101.4 | [W] | PitControl.AutoPit | Rising edge | Auto command | 0 = No command 1 = Set Pit to Auto |  | bool
00101.5 | [W] | PitControl.CallbackAck | Rising edge | Acknowledge of callback (GSM/GPRS only) | 0 = No acknowledge 1 = Callback acknowledge |  | bool
00101.6 | [W] | PitControl.ResetUserDefCounter1 | Rising edge | Reset the user defined counter 1 | 0 = No resetting 1 = Reset counter |  | bool
00101.7 | [W] | PitControl.ResetUserDefCounter2 | Rising edge | Reset the user defined counter 2 | 0 = No resetting 1 = Reset counter |  | bool
00101.8 | [W] | PitControl.ResetUserDefCounter3 | Rising edge | Reset the user defined counter 3 | 0 = No resetting 1 = Reset counter |  | bool
00101.9 | [W] | PitControl.CallBackTest | Rising edge | Activates the Call-back test function | 0 = No command 1 = Activates call-back test |  | bool
00102.0 | [W] | CustomRelayOnOff | On value change | Setting of the custom relay | 0 = Off 1 = On |  | bool
00102.1 | [W] | CustomRelayPulse | Rising edge | Pulse relay (DC Mk 1.5 only) | 0 = No pulse 1 = Pulse |  | bool
00103 | [W] | PitPump1Control | On value change | Manual control of pit pump 1 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00104 | [W] | PitPump2Control | On value change | Manual control of pit pump 2 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00105 | [W] | PitPump3Control | On value change | Manual control of pit pump 3 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00106 | [W] | PitPump4Control | On value change | Manual control of pit pump 4 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00107 | [W] | PitPump5Control | On value change | Manual control of pit pump 5 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00108 | [W] | PitPump6Control | On value change | Manual control of pit pump 6 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00109 | [W] | ScadaPinCode | On value change | 4-digit PIN code set in CU 36x |  |  | unscaled
00110 | [W] | SetEventLogClearID | On value change | Selects last record in event log record to clear |  |  | unscaled
00111 | [W] | SetInterlockTimeout | On value change | Set Interlock Timeout value |  | 1 | min
00112 | [W] | SetRealTimeClockHI | On value change | Set Real Time Clock (32 bit UNIX format) high order |  | 1 | s
00113 | [W] | SetRealTimeClockLO | On value change | Set Real Time Clock (32 bit UNIX format) low order. This triggers the update. |  |  | s
00114 | [W] | SetRtcSecond | On value change | Set Real Time Clock (Seconds) |  |  | enum
00115 | [W] | SetRtcMinute | On value change | Set Real Time Clock (Minutes) |  |  | enum
00116 | [W] | SetRtcHour | On value change | Set Real Time Clock (Hours) |  |  | enum
00117 | [W] | SetRtcDay | On value change | Set Real Time Clock (Day) |  |  | enum
00118 | [W] | SetRtcMonth | On value change | Set Real Time Clock (Month) |  |  | enum
00119 | [W] | SetRtcYear | On value change | Set Real Time Clock (Year - after 2000) |  |  | enum
00120.0 | [W] | SetRtc | Rising edge | Set Real Time Clock (Normal format) | 0 = No command 1 = Set the clock |  | bool
00121 | [W] | SetOverFlowLevel | On value change | Set over flow level |  | 0.01 | m
00122 | [W] | SetHighLevel | On value change | Set high level |  | 0.01 | m
00123 | [W] | SetAlarmLevel | On value change | Set alarm level |  | 0.01 | m
00124 | [W] | SetDryRunningLevel | On value change | Set dry running level |  | 0.01 | m
00125 | [W] | SetFoamDrainingLevel | On value change | Set foam draining level |  | 0.01 | m
00126 | [W] | SetStartLevelPump1 | On value change | Set start level pump 1 |  | 0.01 | m
00127 | [W] | SetStopLevelPump1 | On value change | Set stop level pump1 |  | 0.01 | m
00128 | [W] | SetStartLevelPump2 | On value change | Set start level pump 2 |  | 0.01 | m
00129 | [W] | SetStopLevelPump2 | On value change | Set stop level pump 2 |  | 0.01 | m
00130 | [W] | SetStartLevelPump3 | On value change | Set start level pump 3 |  | 0.01 | m
00131 | [W] | SetStopLevelPump3 | On value change | Set stop level pump 3 |  | 0.01 | m
00132 | [W] | SetStartLevelPump4 | On value change | Set start level pump 4 |  | 0.01 | m
00133 | [W] | SetStopLevelPump4 | On value change | Set stop level pump 4 |  | 0.01 | m
00134 | [W] | SetStartLevelPump5 | On value change | Set start level pump 5 |  | 0.01 | m
00135 | [W] | SetStopLevelPump5 | On value change | Set stop level pump 5 |  | 0.01 | m
00136 | [W] | SetStartLevelPump6 | On value change | Set start level pump 6 |  | 0.01 | m
00137 | [W] | SetStopLevelPump6 | On value change | Set stop level pump 6 |  | 0.01 | m
00138 | [W] | SetCurrentMaxAlarmGrp1 | On value change | Set current max alarm for group 1 |  | 0.1 | A
00139 | [W] | SetCurrentMinAlarmGrp1 | On value change | Set current min alarm for group 1 |  | 0.1 | A
00140 | [W] | SetCurrentMaxWarnGrp1 | On value change | Set current max warning for group 1 |  | 0.1 | A
00141 | [W] | SetCurrentMinWarnGrp1 | On value change | Set current min warning for group 1 |  | 0.1 | A
00142 | [W] | SetCurrentMaxAlarmGrp2 | On value change | Set current max alarm for group 2 |  | 0.1 | A
00143 | [W] | SetCurrentMinAlarmGrp2 | On value change | Set current min alarm for group 2 |  | 0.1 | A
00144 | [W] | SetCurrentMaxWarnGrp2 | On value change | Set current max warning for group 2 |  | 0.1 | A
00145 | [W] | SetCurrentMinWarnGrp2 | On value change | Set current min warning for group 2 |  | 0.1 | A
00146 | [W] | SetSetpointPump1 |  | Set setpoint for pump 1 |  | 1 | %
00147 | [W] | SetSetpointPump2 |  | Set setpoint for pump 2 |  | 1 | %
00148 | [W] | SetSetpointPump3 |  | Set setpoint for pump 3 |  | 1 | %
00149 | [W] | SetSetpointPump4 |  | Set setpoint for pump 4 |  | 1 | %
00150 | [W] | SetSetpointPump5 |  | Set setpoint for pump 5 |  | 1 | %
00151 | [W] | SetSetpointPump6 |  | Set setpoint for pump 6 |  | 1 | %
00152 | [W] | SetControlModePump1 |  | Set control mode for pump 1 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00153 | [W] | SetControlModePump2 |  | Set control mode for pump 2 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00154 | [W] | SetControlModePump3 |  | Set control mode for pump 3 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00155 | [W] | SetControlModePump4 |  | Set control mode for pump 4 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00156 | [W] | SetControlModePump5 |  | Set control mode for pump 5 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00157 | [W] | SetControlModePump6 |  | Set control mode for pump 6 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00158 | [W] | SetFeedbackSensorTypePump1 |  | Sets the feedback sensor type for pump 1 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00159 | [W] | SetFeedbackSensorTypePump2 |  | Sets the feedback sensor type for pump 2 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00160 | [W] | SetFeedbackSensorTypePump3 |  | Sets the feedback sensor type for pump 3 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00161 | [W] | SetFeedbackSensorTypePump4 |  | Sets the feedback sensor type for pump 4 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00162 | [W] | SetFeedbackSensorTypePump5 |  | Sets the feedback sensor type for pump 5 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00163 | [W] | SetFeedbackSensorTypePump6 |  | Sets the feedback sensor type for pump 6 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00164 | [W] | SetSetpointTypePump1 |  | Sets the setpoint type for pump 1 | 0 = Fixed value 1 = Analog input |  | enum
00165 | [W] | SetSetpointTypePump2 |  | Sets the setpoint type for pump 2 | 0 = Fixed value 1 = Analog input |  | enum
00166 | [W] | SetSetpointTypePump3 |  | Sets the setpoint type for pump 3 | 0 = Fixed value 1 = Analog input |  | enum
00167 | [W] | SetSetpointTypePump4 |  | Sets the setpoint type for pump 4 | 0 = Fixed value 1 = Analog input |  | enum
00168 | [W] | SetSetpointTypePump5 |  | Sets the setpoint type for pump 5 | 0 = Fixed value 1 = Analog input |  | enum
00169 | [W] | SetSetpointTypePump6 |  | Sets the setpoint type for pump 6 | 0 = Fixed value 1 = Analog input |  | enum
00170 | [W] | SetAISetpointSelectPump1 |  | Analog input to use as setpoint for pump 1 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00171 | [W] | SetAISetpointSelectPump2 |  | Analog input to use as setpoint for pump 2 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00172 | [W] | SetAISetpointSelectPump3 |  | Analog input to use as setpoint for pump 3 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00173 | [W] | SetAISetpointSelectPump4 |  | Analog input to use as setpoint for pump 4 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00174 | [W] | SetAISetpointSelectPump5 |  | Analog input to use as setpoint for pump 5 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00175 | [W] | SetAISetpointSelectPump6 |  | Analog input to use as setpoint for pump 6 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00176 | [W] | SetFixedFrequencyPump1 |  | Fixed frequency for pump 1 |  | 0.01 | Hz
00177 | [W] | SetFixedFrequencyPump2 |  | Fixed frequency for pump 2 |  | 0.01 | Hz
00178 | [W] | SetFixedFrequencyPump3 |  | Fixed frequency for pump 3 |  | 0.01 | Hz
00179 | [W] | SetFixedFrequencyPump4 |  | Fixed frequency for pump 4 |  | 0.01 | Hz
00180 | [W] | SetFixedFrequencyPump5 |  | Fixed frequency for pump 5 |  | 0.01 | Hz
00181 | [W] | SetFixedFrequencyPump6 |  | Fixed frequency for pump 6 |  | 0.01 | Hz
00182 | [W] | SetH2SLevel |  | For reception of Hydrogen sulfide (H2S) measurement via GRM |  | 1 | ppm
00183.0 | [W] | SetH2SSensorFaults.SignalFault |  | For reception of H2S sensor signal fault via GRM | 0=No fault 1=Sensor signal fault |  | bool
00184 | [W] | SetDosingRef |  | Set chemical dosing reference for H2S level control |  | 0.1 | ltr/h
STATUS [R]
00201.0 | [R] | Acknowledge.ResetAlarm | 1 = Acknowledged | Acknowledge of Reset Alarm command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.1 | [R] | Acknowledge.SetRtc | 1 = Acknowledged | Acknowledge of Set Real Time Clock command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.2 | [R] | Acknowledge.ResetEventLog | 1 = Acknowledged | Acknowledge of Reset Event Log command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.3 | [R] | Acknowledge.InterlockPit | 1 = Acknowledged | Acknowledge of Interlock command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.4 | [R] | Acknowledge.AutoPit | 1 = Acknowledged | Acknowledge of Auto command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.5 | [R] | Acknowledge.CallBackAck | 1 = Acknowledged | Acknowledge of CallBackAck command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.6 | [R] | Acknowledge.ResetUserDefCounter1 | 1 = Acknowledged | Acknowledge of ResetUserDefCounter1 command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.7 | [R] | Acknowledge.ResetUserDefCounter2 | 1 = Acknowledged | Acknowledge of ResetUserDefCounter2 command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.8 | [R] | Acknowledge.ResetUserDefCounter3 | 1 = Acknowledged | Acknowledge of ResetUserDefCounter3 command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.9 | [R] | Acknowledge.CallBackTest | 1 = Acknowledged | Acknowledge of CallBackTest command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.10 | [R] | Acknowledge.RelayPulse | 1 = Acknowledged | Acknowledge of RelayPulse command | 0 = No acknowledge 1 = Acknowledged |  | bool
00202.1 | [R] | PitStatus.Alarm |  | Presence of an alarm in CU 36x | 0 = No Alarm 1 = Alarm present |  | bool
00202.2 | [R] | PitStatus.Warning |  | Presence of a warning in CU 36x | 0 = No warning 1 = Warning present |  | bool
00202.3 | [R] | PitStatus.ManualControl |  | Manual or auto control | 0 = Auto control 1 = Manual control |  | bool
00202.4 | [R] | PitStatus.ScadaPinCodeEnabled |  | Is SCADA PIN code set in CU 36x? | 0 = Disabled 1 = Enabled |  | bool
00202.5 | [R] | PitStatus.WriteAccess |  | Indicates if remote control (write access) is allowed | 0 = No write access 1 = Write access granted |  | bool
00203 | [R] | PitOperatingMode |  | Actual pit operating mode | 0 = Standby 1 = Start-up delay 2 = Pumping 3 = Stop delay 4 = Pumping max 5 = Stopped 6 = Foam Draining 7 = Daily Emptying 8 = Pump anti seizing 9 = Manual control 10 = Interlock control 11 = Mains failure 12 = Level sensor error 13 = All pumps in alarm 14 = All pumps out of operation 15 = Service mode, alarms surpressed |  | enum
00204.0 | [R] | PitPumpsPresent.Pump1 | Bit interpreted, 1 = Present | Presence of pump 1 | 0 = Not present 1 = Present |  | bool
00204.1 | [R] | PitPumpsPresent.Pump2 | Bit interpreted, 1 = Present | Presence of pump 2 | 0 = Not present 1 = Present |  | bool
00204.2 | [R] | PitPumpsPresent.Pump3 | Bit interpreted, 1 = Present | Presence of pump 3 | 0 = Not present 1 = Present |  | bool
00204.3 | [R] | PitPumpsPresent.Pump4 | Bit interpreted, 1 = Present | Presence of pump 4 | 0 = Not present 1 = Present |  | bool
00204.4 | [R] | PitPumpsPresent.Pump5 | Bit interpreted, 1 = Present | Presence of pump 5 | 0 = Not present 1 = Present |  | bool
00204.5 | [R] | PitPumpsPresent.Pump6 | Bit interpreted, 1 = Present | Presence of pump 6 | 0 = Not present 1 = Present |  | bool
00204.6 | [R] | PitPumpsPresent.Mixer | Bit interpreted, 1 = Present | Presence of mixer | 0 = Not present 1 = Present |  | bool
00205.0 | [R] | PitPumpsDisabled.Pump1 | Bit interpreted, 1 = Disabled | Enabled/Disabled status of pump 1 | 0 = Enabled 1 = Disabled |  | bool
00205.1 | [R] | PitPumpsDisabled.Pump2 | Bit interpreted, 1 = Disabled | Enabled/Disabled status of pump 2 | 0 = Enabled 1 = Disabled |  | bool
00205.2 | [R] | PitPumpsDisabled.Pump3 | Bit interpreted, 1 = Disabled | Enabled/Disabled status of pump 3 | 0 = Enabled 1 = Disabled |  | bool
00205.3 | [R] | PitPumpsDisabled.Pump4 | Bit interpreted, 1 = Disabled | Enabled/Disabled status of pump 4 | 0 = Enabled 1 = Disabled |  | bool
00205.4 | [R] | PitPumpsDisabled.Pump5 | Bit interpreted, 1 = Disabled | Enabled/Disabled status of pump 5 | 0 = Enabled 1 = Disabled |  | bool
00205.5 | [R] | PitPumpsDisabled.Pump6 | Bit interpreted, 1 = Disabled | Enabled/Disabled status of pump 6 | 0 = Enabled 1 = Disabled |  | bool
00205.6 | [R] | PitPumpsDisabled.Mixer | Bit interpreted, 1 = Disabled | Enabled/Disabled status of mixer | 0 = Enabled 1 = Disabled |  | bool
00206.0 | [R] | PitPumpsRunning.Pump1 | Bit interpreted, 1 = Running | Rotation status of pump 1 | 0 = Not running (or not present) 1 = Running |  | bool
00206.1 | [R] | PitPumpsRunning.Pump2 | Bit interpreted, 1 = Running | Rotation status of pump 2 | 0 = Not running (or not present) 1 = Running |  | bool
00206.2 | [R] | PitPumpsRunning.Pump3 | Bit interpreted, 1 = Running | Rotation status of pump 3 | 0 = Not running (or not present) 1 = Running |  | bool
00206.3 | [R] | PitPumpsRunning.Pump4 | Bit interpreted, 1 = Running | Rotation status of pump 4 | 0 = Not running (or not present) 1 = Running |  | bool
00206.4 | [R] | PitPumpsRunning.Pump5 | Bit interpreted, 1 = Running | Rotation status of pump 5 | 0 = Not running (or not present) 1 = Running |  | bool
00206.5 | [R] | PitPumpsRunning.Pump6 | Bit interpreted, 1 = Running | Rotation status of pump 6 | 0 = Not running (or not present) 1 = Running |  | bool
00206.6 | [R] | PitPumpsRunning.Mixer | Bit interpreted, 1 = Running | Rotation status of mixer | 0 = Not running (or not present) 1 = Running |  | bool
00207.0 | [R] | PitPumpsMonitoringFault.Pump1 | Bit interpreted, 1 = Monitor Fault | Monitoring fault on pump 1 | 0 = No monitoring fault 1 = Monitoring fault |  | bool
00207.1 | [R] | PitPumpsMonitoringFault.Pump2 | Bit interpreted, 1 = Monitor Fault | Monitoring fault on pump 2 | 0 = No monitoring fault 1 = Monitoring fault |  | bool
00207.2 | [R] | PitPumpsMonitoringFault.Pump3 | Bit interpreted, 1 = Monitor Fault | Monitoring fault on pump 3 | 0 = No monitoring fault 1 = Monitoring fault |  | bool
00207.3 | [R] | PitPumpsMonitoringFault.Pump4 | Bit interpreted, 1 = Monitor Fault | Monitoring fault on pump 4 | 0 = No monitoring fault 1 = Monitoring fault |  | bool
00207.4 | [R] | PitPumpsMonitoringFault.Pump5 | Bit interpreted, 1 = Monitor Fault | Monitoring fault on pump 5 | 0 = No monitoring fault 1 = Monitoring fault |  | bool
00207.5 | [R] | PitPumpsMonitoringFault.Pump6 | Bit interpreted, 1 = Monitor Fault | Monitoring fault on pump 6 | 0 = No monitoring fault 1 = Monitoring fault |  | bool
00207.6 | [R] | PitPumpsMonitoringFault.Mixer | Bit interpreted, 1 = Monotor Fault | Monitoring fault on mixer | 0 = No monitoring fault 1 = Monitoring fault |  | bool
00208.0 | [R] | PitPumpsWarning.Pump1 | Bit interpreted, 1 = Warning | Warning on pump 1 | 0 = No warning 1 = Warning |  | bool
00208.1 | [R] | PitPumpsWarning.Pump2 | Bit interpreted, 1 = Warning | Warning on pump 2 | 0 = No warning 1 = Warning |  | bool
00208.2 | [R] | PitPumpsWarning.Pump3 | Bit interpreted, 1 = Warning | Warning on pump 3 | 0 = No warning 1 = Warning |  | bool
00208.3 | [R] | PitPumpsWarning.Pump4 | Bit interpreted, 1 = Warning | Warning on pump 4 | 0 = No warning 1 = Warning |  | bool
00208.4 | [R] | PitPumpsWarning.Pump5 | Bit interpreted, 1 = Warning | Warning on pump 5 | 0 = No warning 1 = Warning |  | bool
00208.5 | [R] | PitPumpsWarning.Pump6 | Bit interpreted, 1 = Warning | Warning on pump 6 | 0 = No warning 1 = Warning |  | bool
00208.6 | [R] | PitPumpsWarning.Mixer | Bit interpreted, 1 = Warning | Warning on mixer | 0 = No warning 1 = Warning |  | bool
00209.0 | [R] | PitPumpsAlarm.Pump1 | Bit interpreted, 1 = Fault | Alarm on pump 1 | 0 = No alarm 1 = Fault |  | bool
00209.1 | [R] | PitPumpsAlarm.Pump2 | Bit interpreted, 1 = Fault | Alarm on pump 2 | 0 = No alarm 1 = Fault |  | bool
00209.2 | [R] | PitPumpsAlarm.Pump3 | Bit interpreted, 1 = Fault | Alarm on pump 3 | 0 = No alarm 1 = Fault |  | bool
00209.3 | [R] | PitPumpsAlarm.Pump4 | Bit interpreted, 1 = Fault | Alarm on pump 4 | 0 = No alarm 1 = Fault |  | bool
00209.4 | [R] | PitPumpsAlarm.Pump5 | Bit interpreted, 1 = Fault | Alarm on pump 5 | 0 = No alarm 1 = Fault |  | bool
00209.5 | [R] | PitPumpsAlarm.Pump6 | Bit interpreted, 1 = Fault | Alarm on pump 6 | 0 = No alarm 1 = Fault |  | bool
00209.6 | [R] | PitPumpsAlarm.Mixer | Bit interpreted, 1 = Fault | Alarm on mixer | 0 = No alarm 1 = Fault |  | bool
00210.0 | [R] | PitAlarms1.Overflow alarm |  | Overflow alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.1 | [R] | PitAlarms1.High level alarm |  | High level alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.2 | [R] | PitAlarms1.Alarm Level |  | Alarm level | 0 = No Alarm 1 = Alarm present |  | bool
00210.3 | [R] | PitAlarms1.Dry running |  | Dry running alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.4 | [R] | PitAlarms1.Mains supply fault |  | Mains supply fault alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.5 | [R] | PitAlarms1.Float switch sequence inconsistency |  | Float switch sequence inconsistency | 0 = No Alarm 1 = Alarm present |  | bool
00210.6 | [R] | PitAlarms1.Inconsistency (switches/sensor) |  | Sensor/switches Inconsistency alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.7 | [R] | PitAlarms1.Level/pressure sensor signal fault |  | Level/pressure sensor signal alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.8 | [R] | PitAlarms1.Flow sensor signal fault |  | Flow sensor signal alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.9 | [R] | PitAlarms1.Power meter sensor signal fault |  | Power meter sensor signal alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.10 | [R] | PitAlarms1.Mixer contactor feedback fault |  | Mixer contactor alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.11 | [R] | PitAlarms1.Distributed I/O module comm. Fault |  | I/O module communication alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.12 | [R] | PitAlarms1.Add-on CIM comm. Fault |  | Connection between CU 36x and CIM module | 0 = No Alarm 1 = Alarm present |  | bool
00210.13 | [R] | PitAlarms1.SIM card fault |  | SIM card alarm (GSM/GPRS only) | 0 = No Alarm 1 = Alarm present |  | bool
00210.14 | [R] | PitAlarms1.SCADA Call-back fault |  | SCADA call-back alarm | 0 = No Alarm 1 = Alarm present |  | bool
00210.15 | [R] | PitAlarms1.Power on occurred |  | Power on occured alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.0 | [R] | PitAlarms2.Battery/UPS fault |  | Battery alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.1 | [R] | PitAlarms2.Hardware fault (general) |  | Hardware fault alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.2 | [R] | PitAlarms2.Ethernet No IP address from DHCP server |  | Missing IP address alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.3 | [R] | PitAlarms2.Ethernet Auto disabled due to misuse |  | Ethernet misuse alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.4 | [R] | PitAlarms2.Mixer time for service |  | Time to service the mixer alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.5 | [R] | PitAlarms2.Mixer max no. of starts pr. hour exceeded |  | Too many mixer starts pr. hour alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.6 | [R] | PitAlarms2.Custom relay activated |  | Custom relay activated alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.7 | [R] | PitAlarms2.RESERVED |  |  |  |  | bool
00211.8 | [R] | PitAlarms2.External Fault |  | External alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.9 | [R] | PitAlarms2.Combi Event No. 1 |  | Combi event 1 alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.10 | [R] | PitAlarms2.Combi Event No. 2 |  | Combi event 2 alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.11 | [R] | PitAlarms2.Combi Event No. 3 |  | Combi event 3 alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.12 | [R] | PitAlarms2.Combi Event No. 4 |  | Combi event 4 alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.13 | [R] | PitAlarms2.AI sensor 1 signal fault |  | AI sensor 1 signal fault alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.14 | [R] | PitAlarms2.AI sensor 2signal fault |  | AI sensor 2 signal fault alarm | 0 = No Alarm 1 = Alarm present |  | bool
00211.15 | [R] | PitAlarms2.AI sensor 3 signal fault |  | AI sensor 3 signal fault alarm | 0 = No Alarm 1 = Alarm present |  | bool
00212.0 | [R] | PitAlarms3.DischargePressureSignalFault |  | Discharge pressure sensor signal fault | 0 = No Alarm 1 = Alarm present |  | bool
00212.1 | [R] | PitAlarms3.WaterOnFloor |  | Water on floor alarm | 0 = No Alarm 1 = Alarm present |  | bool
00212.2 | [R] | PitAlarms3.GasDetected |  | Gas detected alarm | 0 = No Alarm 1 = Alarm present |  | bool
00212.3 | [R] | PitAlarms3.UserEvent1 |  | User event 1 alarm | 0 = No Alarm 1 = Alarm present |  | bool
00212.4 | [R] | PitAlarms3.UserEvent2 |  | User event 2 alarm | 0 = No Alarm 1 = Alarm present |  | bool
00212.5 | [R] | PitAlarms3.UserEvent3 |  | User event 3 alarm | 0 = No Alarm 1 = Alarm present |  | bool
00212.6 | [R] | PitAlarms3.UserEvent4 |  | User event 4 alarm | 0 = No Alarm 1 = Alarm present |  | bool
00212.7 | [R] | PitAlarms3.H2SSensorSignalFault |  | Hydrogen sulfide (H2S ) sensor signal fault | 0 = No Alarm 1 = Alarm present |  | bool
00213.0 | [R] | PitWarnings1.Overflow alarm |  | Overflow warning | 0 = No warning 1 = Warning present |  | bool
00213.1 | [R] | PitWarnings1.High level alarm |  | High level warning | 0 = No warning 1 = Warning present |  | bool
00213.2 | [R] | PitWarnings1.Alarm Level |  | Alarm level warning | 0 = No warning 1 = Warning present |  | bool
00213.3 | [R] | PitWarnings1.Dry running |  | Dry running warning | 0 = No warning 1 = Warning present |  | bool
00213.4 | [R] | PitWarnings1.Mains supply fault |  | Mains supply fault | 0 = No warning 1 = Warning present |  | bool
00213.5 | [R] | PitWarnings1.Float switch sequence inconsistency |  | Inconsistency in float switch sequence | 0 = No warning 1 = Warning present |  | bool
00213.6 | [R] | PitWarnings1.Inconsistency (switches/sensor) |  | Inconsistency in switches or sensor | 0 = No warning 1 = Warning present |  | bool
00213.7 | [R] | PitWarnings1.Level/pressure sensor signal fault |  | Level/pressure sensor signal warning | 0 = No warning 1 = Warning present |  | bool
00213.8 | [R] | PitWarnings1.Flow sensor signal fault |  | Flow sensor signal warning | 0 = No warning 1 = Warning present |  | bool
00213.9 | [R] | PitWarnings1.Power meter sensor signal fault |  | Power meter sensor signal warning | 0 = No warning 1 = Warning present |  | bool
00213.10 | [R] | PitWarnings1.Mixer contactor feedback fault |  | Mixer contactor warning | 0 = No warning 1 = Warning present |  | bool
00213.11 | [R] | PitWarnings1.Distributed I/O module comm. Fault |  | I/O module communication warning | 0 = No warning 1 = Warning present |  | bool
00213.12 | [R] | PitWarnings1.Add-on CIM comm. Fault |  | Connection between CU 36x and CIM module | 0 = No warning 1 = Warning present |  | bool
00213.13 | [R] | PitWarnings1.SIM card fault |  | SIM card warning (GSM/GPRS only) | 0 = No warning 1 = Warning present |  | bool
00213.14 | [R] | PitWarnings1.SCADA Call-back fault |  | SCADA call-back warning | 0 = No warning 1 = Warning present |  | bool
00213.15 | [R] | PitWarnings1.Power on occurred |  | Power on occured warning | 0 = No warning 1 = Warning present |  | bool
00214.0 | [R] | PitWarnings2.Battery/UPS fault |  | Battery warning | 0 = No warning 1 = Warning present |  | bool
00214.1 | [R] | PitWarnings2.Hardware fault (general) |  | Hardware fault | 0 = No warning 1 = Warning present |  | bool
00214.2 | [R] | PitWarnings2.Ethernet No IP address from DHCP server |  | Missing IP address | 0 = No warning 1 = Warning present |  | bool
00214.3 | [R] | PitWarnings2.Ethernet Auto disabled due to misuse |  | Ethernet misuse | 0 = No warning 1 = Warning present |  | bool
00214.4 | [R] | PitWarnings2.Mixer time for service |  | Time to service the mixer | 0 = No warning 1 = Warning present |  | bool
00214.5 | [R] | PitWarnings2.Mixer max no. of starts pr. hour exceeded |  | Too many mixer starts pr. hour | 0 = No warning 1 = Warning present |  | bool
00214.6 | [R] | PitWarnings2.Custom relay activated |  | Custom relay | 0 = No warning 1 = Warning present |  | bool
00214.7 | [R] | PitWarnings2.RESERVED |  |  |  |  | bool
00214.8 | [R] | PitWarnings2.External Fault |  | External warning | 0 = No warning 1 = Warning present |  | bool
00214.9 | [R] | PitWarnings2.Combi Event No. 1 |  | Combi event 1 | 0 = No warning 1 = Warning present |  | bool
00214.10 | [R] | PitWarnings2.Combi Event No. 2 |  | Combi event 2 | 0 = No warning 1 = Warning present |  | bool
00214.11 | [R] | PitWarnings2.Combi Event No. 3 |  | Combi event 3 | 0 = No warning 1 = Warning present |  | bool
00214.12 | [R] | PitWarnings2.Combi Event No. 4 |  | Combi event 4 | 0 = No warning 1 = Warning present |  | bool
00214.13 | [R] | PitWarnings2.AI sensor 1 signal fault |  | AI sensor 1 warning | 0 = No warning 1 = Warning present |  | bool
00214.14 | [R] | PitWarnings2.AI sensor 2signal fault |  | AI sensor 2 warning | 0 = No warning 1 = Warning present |  | bool
00214.15 | [R] | PitWarnings2.AI sensor 3 signal fault |  | AI sensor 3 warning | 0 = No warning 1 = Warning present |  | bool
00215.0 | [R] | PitWarnings3.DischargePressureSignalFault |  | Discharge pressure sensor signal fault | 0 = No warning 1 = Warning present |  | bool
00215.1 | [R] | PitWarnings3.WaterOnFloor |  | Water on floor warning | 0 = No warning 1 = Warning present |  | bool
00215.2 | [R] | PitWarnings3.GasDetected |  | Gas detected warning | 0 = No warning 1 = Warning present |  | bool
00215.3 | [R] | PitWarnings3.UserEvent1 |  | User event 1 warning | 0 = No warning 1 = Warning present |  | bool
00215.4 | [R] | PitWarnings3.UserEvent2 |  | User event 2 warning | 0 = No warning 1 = Warning present |  | bool
00215.5 | [R] | PitWarnings3.UserEvent3 |  | User event 3 warning | 0 = No warning 1 = Warning present |  | bool
00215.6 | [R] | PitWarnings3.UserEvent4 |  | User event 4 warning | 0 = No warning 1 = Warning present |  | bool
00216 | [R] | EventLogLatestID |  | Latest ID of event log |  |  | unscaled
00217 | [R] | NumberOfFloatSwitches |  | Amount of float switches in system |  |  | unscaled
00218.0 | [R] | FloatSwitchesStatus.Switch1 |  | Status of float switch 1 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00218.1 | [R] | FloatSwitchesStatus.Switch2 |  | Status of float switch 2 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00218.2 | [R] | FloatSwitchesStatus.Switch3 |  | Status of float switch 3 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00218.3 | [R] | FloatSwitchesStatus.Switch4 |  | Status of float switch 4 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00218.4 | [R] | FloatSwitchesStatus.Switch5 |  | Status of float switch 5 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00218.5 | [R] | FloatSwitchesStatus.ExtraOverflowSwitch |  | Status of extra overflow float switch | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00219 | [R] | FloatSwitch1Function |  | Function of float switch 1 | 0 = Not used 1 = Dry running 3 = Stop all pumps 4 = Stop 5 = Stop 1 (1st pump) 6 = Stop 2 (2nd pump) 7 = Stop 3 (3rd pump) 8 = Stop 4 (4th pump) 9 = Stop 5 (5th pump) 10 = Stop 6 (6th pump) 11 = Start/Stop 12 = Start 1 / Stop 13 = Start 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 16 = Start 3 (3rd pump) 17 = Start 4 (4th pump) 18 = Start 5 (5th pump) 19 = Start 6 (6th pump) 20 = Start all 21 = Alarm level 23 = High water 255 = Not available 65535 = Not available |  | enum
00220 | [R] | FloatSwitch2Function |  | Function of float switch 2 | 0 = Not used 1 = Dry running 3 = Stop all pumps 4 = Stop 5 = Stop 1 (1st pump) 6 = Stop 2 (2nd pump) 7 = Stop 3 (3rd pump) 8 = Stop 4 (4th pump) 9 = Stop 5 (5th pump) 10 = Stop 6 (6th pump) 11 = Start/Stop 12 = Start 1 / Stop 13 = Start 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 16 = Start 3 (3rd pump) 17 = Start 4 (4th pump) 18 = Start 5 (5th pump) 19 = Start 6 (6th pump) 20 = Start all 21 = Alarm level 23 = High water 255 = Not available 65535 = Not available |  | enum
00221 | [R] | FloatSwitch3Function |  | Function of float switch 3 | 0 = Not used 1 = Dry running 3 = Stop all pumps 4 = Stop 5 = Stop 1 (1st pump) 6 = Stop 2 (2nd pump) 7 = Stop 3 (3rd pump) 8 = Stop 4 (4th pump) 9 = Stop 5 (5th pump) 10 = Stop 6 (6th pump) 11 = Start/Stop 12 = Start 1 / Stop 13 = Start 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 16 = Start 3 (3rd pump) 17 = Start 4 (4th pump) 18 = Start 5 (5th pump) 19 = Start 6 (6th pump) 20 = Start all 21 = Alarm level 23 = High water 255 = Not available 65535 = Not available |  | enum
00222 | [R] | FloatSwitch4Function |  | Function of float switch 4 | 0 = Not used 1 = Dry running 3 = Stop all pumps 4 = Stop 5 = Stop 1 (1st pump) 6 = Stop 2 (2nd pump) 7 = Stop 3 (3rd pump) 8 = Stop 4 (4th pump) 9 = Stop 5 (5th pump) 10 = Stop 6 (6th pump) 11 = Start/Stop 12 = Start 1 / Stop 13 = Start 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 16 = Start 3 (3rd pump) 17 = Start 4 (4th pump) 18 = Start 5 (5th pump) 19 = Start 6 (6th pump) 20 = Start all 21 = Alarm level 23 = High water 255 = Not available 65535 = Not available |  | enum
00223 | [R] | FloatSwitch5Function |  | Function of float switch 5 | 0 = Not used 1 = Dry running 3 = Stop all pumps 4 = Stop 5 = Stop 1 (1st pump) 6 = Stop 2 (2nd pump) 7 = Stop 3 (3rd pump) 8 = Stop 4 (4th pump) 9 = Stop 5 (5th pump) 10 = Stop 6 (6th pump) 11 = Start/Stop 12 = Start 1 / Stop 13 = Start 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 16 = Start 3 (3rd pump) 17 = Start 4 (4th pump) 18 = Start 5 (5th pump) 19 = Start 6 (6th pump) 20 = Start all 21 = Alarm level 23 = High water 255 = Not available 65535 = Not available |  | enum
00224.0 | [R] | PitSensors.UltrasonicLevelControlSensor |  | Presence of ultrasonic level sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.1 | [R] | PitSensors.PressureSensor |  | Presence of pressure level sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.2 | [R] | PitSensors.FloatSwitches |  | Presence of float switches | 0 = Float switches not present 1 = Float switches present |  | bool
00224.3 | [R] | PitSensors.FlowSensor |  | Presence of flow sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.4 | [R] | Pitsensors.Power/EnergySensor |  | Presence of power/energy sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.5 | [R] | Pitsensors.UserDefinedAIsensor1present |  | Presence of AI sensor 1 | 0 = Sensor not present 1 = Sensor present |  | bool
00224.6 | [R] | Pitsensors.UserDefinedAIsensor2present |  | Presence of AI sensor 2 | 0 = Sensor not present 1 = Sensor present |  | bool
00224.7 | [R] | Pitsensors.UserDefinedAIsensor3present |  | Presence of AI sensor 3 | 0 = Sensor not present 1 = Sensor present |  | bool
00225 | [R] | DayCounterZeroTime |  | Zero-time of the day (0-23) |  |  | enum
00226 | [R] | InterlockTimeout |  | Timeout for interlock in seconds |  | 1 | s
00227 | [R] | InterlockRemainTime |  | Remaining interlock time in seconds |  | 1 | s
00228 | [R] | UNIXRealTimeClockHI |  | Real Time Clock (32 bit UNIX format) |  | 1 | s
00229 | [R] | UNIXRealTimeClockLO
00230 | [R] | RtcSecond |  | Real time clock - Seconds |  |  | enum
00231 | [R] | RtcMinute |  | Real time clock - Minutes |  |  | enum
00232 | [R] | RtcHour |  | Real time clock - Hours |  |  | enum
00233 | [R] | RtcDay |  | Real time clock - Day of month |  |  | enum
00234 | [R] | RtcMonth |  | Real time clock - Month |  |  | enum
00235 | [R] | RtcYear |  | Real time clock - Year (after 2000) |  |  | enum
00236 | [R] | GSMSignalLevelActual |  | Actual GSM signal level |  | 1 | %
00237 | [R] | GSMSignalLevelAverage |  | Average GSM signal level |  | 1 | %
00238 | [R] | IPAddressHI |  | High order part of IP address |  |  | IP
00239 | [R] | IPAddressLO |  | Low order part of IP address |  |  | IP
00240 | [R] | OverFlowLevel |  | Actual overflow level |  | 0.01 | m
00241 | [R] | HighLevel |  | Actual high level |  | 0.01 | m
00242 | [R] | AlarmLevel |  | Actual alarm level |  | 0.01 | m
00243 | [R] | DryRunningLevel |  | Actual dry running level |  | 0.01 | m
00244 | [R] | FoamDrainingLevel |  | Actual foam draining level |  | 0.01 | m
00245 | [R] | StartLevelPump1 |  | Actual start level of pump 1 |  | 0.01 | m
00246 | [R] | StopLevelPump1 |  | Actual stop level of pump 1 |  | 0.01 | m
00247 | [R] | StartLevelPump2 |  | Actual start level of pump 2 |  | 0.01 | m
00248 | [R] | StopLevelPump2 |  | Actual stop level of pump 2 |  | 0.01 | m
00249 | [R] | StartLevelPump3 |  | Actual start level of pump 3 |  | 0.01 | m
00250 | [R] | StopLevelPump3 |  | Actual stop level of pump 3 |  | 0.01 | m
00251 | [R] | StartLevelPump4 |  | Actual start level of pump 4 |  | 0.01 | m
00252 | [R] | StopLevelPump4 |  | Actual stop level of pump 4 |  | 0.01 | m
00253 | [R] | StartLevelPump5 |  | Actual start level of pump 5 |  | 0.01 | m
00254 | [R] | StopLevelPump5 |  | Actual stop level of pump 5 |  | 0.01 | m
00255 | [R] | StartLevelPump6 |  | Actual start level of pump 6 |  | 0.01 | m
00256 | [R] | StopLevelPump6 |  | Actual stop level of pump 6 |  | 0.01 | m
00257 | [R] | FirstGroup2Pump |  | First pump in group 2 | 0 = - 1 = - 2 = Pump2 3 = Pump 3 4 = Pump 4 5 = Pump 5 6 = Pump 6 255 = No grouping 65535 = Not available |  | enum
00258 | [R] | BatteryVoltage |  | Voltage on the battery |  | 0.1 | V
00259.0 | [R] | IOLogicOutput1 |  | IO Logic output 1 | 0 = Off 1 = On |  | bool
00259.1 | [R] | IOLogicOutput2 |  | IO Logic output 2 | 0 = Off 1 = On |  | bool
00259.2 | [R] | IOLogicOutput3 |  | IO Logic output 3 | 0 = Off 1 = On |  | bool
00259.3 | [R] | IOLogicOutput4 |  | IO Logic output 4 | 0 = Off 1 = On |  | bool
00259.4 | [R] | IOLogicOutput5 |  | IO Logic output 5 | 0 = Off 1 = On |  | bool
00259.5 | [R] | IOLogicOutput6 |  | IO Logic output 6 | 0 = Off 1 = On |  | bool
00259.6 | [R] | IOLogicOutput7 |  | IO Logic output 7 | 0 = Off 1 = On |  | bool
00259.7 | [R] | IOLogicOutput8 |  | IO Logic output 8 | 0 = Off 1 = On |  | bool
00260 | [R] | RandomStartLevelBand |  | Random start level band |  | 0.01 | m
00261 | [R] | ActualCurrentMaxAlarmGrp1 | On value change | Actual current max alarm for group 1 |  | 0.1 | A
00262 | [R] | ActualCurrentMinAlarmGrp1 | On value change | Actual current min alarm for group 1 |  | 0.1 | A
00263 | [R] | ActualCurrentMaxWarnGrp1 | On value change | Actual current max warning for group 1 |  | 0.1 | A
00264 | [R] | ActualCurrentMinWarnGrp1 | On value change | Actual current min warning for group 1 |  | 0.1 | A
00265 | [R] | ActualCurrentMaxAlarmGrp2 | On value change | Actual current max alarm for group 2 |  | 0.1 | A
00266 | [R] | ActualCurrentMinAlarmGrp2 | On value change | Actual current min alarm for group 2 |  | 0.1 | A
00267 | [R] | ActualCurrentMaxWarnGrp2 | On value change | Actual current max warning for group 2 |  | 0.1 | A
00268 | [R] | ActualCurrentMinWarnGrp2 | On value change | Actual current min warning for group 2 |  | 0.1 | A
00269.0 | [R] | PitAlarms4.OverPressureAlarm |  | Dosing pump over pressure alarm | 0 = No Alarm 1 = Alarm present |  | bool
00269.1 | [R] | PitAlarms4.UnderPressureAlarm |  | Dosing pump mean pressure to low (Under pressure). | 0 = No Alarm 1 = Alarm present |  | bool
00269.2 | [R] | PitAlarms4.DeaeratingProblemAlarm |  | Gas in dosing pump head, deaerating problem | 0 = No Alarm 1 = Alarm present |  | bool
00269.3 | [R] | PitAlarms4.CavitationAlarm |  | Dosing pump cavitation | 0 = No Alarm 1 = Alarm present |  | bool
00269.4 | [R] | PitAlarms4.PressureValveLeakageAlarm |  | Dosing pump pressure valve leakage | 0 = No Alarm 1 = Alarm present |  | bool
00269.5 | [R] | PitAlarms4.SuctionValveLeakageAlarm |  | Dosing pump suction valve leakage | 0 = No Alarm 1 = Alarm present |  | bool
00269.6 | [R] | PitAlarms4.VentingValveDefectAlarm |  | Dosing pump venting valve defect | 0 = No Alarm 1 = Alarm present |  | bool
00269.7 | [R] | PitAlarms4.TimeForServiceAlarm |  | Dosing pump time for service is exceed | 0 = No Alarm 1 = Alarm present |  | bool
00269.8 | [R] | PitAlarms4.SoonTimeForServiceAlarm |  | Dosing pump soon time for service | 0 = No Alarm 1 = Alarm present |  | bool
00269.9 | [R] | PitAlarms4.CapacityTooLowAlarm |  | Dosing pump capacity too low (Perform. requirement not met) | 0 = No Alarm 1 = Alarm present |  | bool
00269.10 | [R] | PitAlarms4.DiaphragmBreakAlarm |  | Dosing pump diaphragm break | 0 = No Alarm 1 = Alarm present |  | bool
00269.11 | [R] | PitAlarms4.BlockedAlarm |  | Dosing pump blocked motor/pump | 0 = No Alarm 1 = Alarm present |  | bool
00269.12 | [R] | PitAlarms4.PreemptyTankAlarm |  | Dosing pump pre empty tank | 0 = No Alarm 1 = Alarm present |  | bool
00269.13 | [R] | PitAlarms4.EmptyTankAlarm |  | Dosing pump empty tank (Dry Running) | 0 = No Alarm 1 = Alarm present |  | bool
00269.14 | [R] | PitAlarms4.CableBreakFlowMonitorAlarm |  | Dosing pump cable breakdown on Flow Monitor (Flow sensor sig. fault) | 0 = No Alarm 1 = Alarm present |  | bool
00269.15 | [R] | PitAlarms4.CableBreakAnalogRefAlarm |  | Cable breakdown on Analogue (Reference input sig. fault) | 0 = No Alarm 1 = Alarm present |  | bool
00270.0 | [R] | PitWarn4.OverPressureWarn |  | Dosing pump over pressure | 0 = No Warning 1 = Warning present |  | bool
00270.1 | [R] | PitWarn4.UnderPressureWarn |  | Dosing pump mean pressure to low (Under pressure). | 0 = No Warning 1 = Warning present |  | bool
00270.2 | [R] | PitWarn4.DeaeratingProblemWarn |  | Dosing pump gas in pump head, deaerating problem | 0 = No Warning 1 = Warning present |  | bool
00270.3 | [R] | PitWarn4.CavitationWarn |  | Dosing pump cavitation | 0 = No Warning 1 = Warning present |  | bool
00270.4 | [R] | PitWarn4.PressureValveLeakageWarn |  | Dosing pump pressure valve leakage | 0 = No Warning 1 = Warning present |  | bool
00270.5 | [R] | PitWarn4.SuctionValveLeakageWarn |  | Dosing pump suction valve leakage | 0 = No Warning 1 = Warning present |  | bool
00270.6 | [R] | PitWarn4.VentingValveDefectWarn |  | Dosing pump venting valve defect | 0 = No Warning 1 = Warning present |  | bool
00270.7 | [R] | PitWarn4.TimeForServiceWarn |  | Dosing pump time for service is exceed | 0 = No Warning 1 = Warning present |  | bool
00270.8 | [R] | PitWarn4.SoonTimeForServiceWarn |  | Dosing pump soon time for service | 0 = No Warning 1 = Warning present |  | bool
00270.9 | [R] | PitWarn4.CapacityTooLowWarn |  | Dosing pump capacity too low (Perform. requirem. not met) | 0 = No Warning 1 = Warning present |  | bool
00270.10 | [R] | PitWarn4.DiaphragmBreakWarn |  | Dosing pump diaphragm break | 0 = No Warning 1 = Warning present |  | bool
00270.11 | [R] | PitWarn4.BlockedWarn |  | Dosing pump blocked motor/pump | 0 = No Warning 1 = Warning present |  | bool
00270.12 | [R] | PitWarn4.PreemptyTankWarn |  | Dosing pump pre empty tank | 0 = No Warning 1 = Warning present |  | bool
00270.13 | [R] | PitWarn4.EmptyTankWarn |  | Dosing pump empty tank (Dry Running) | 0 = No Warning 1 = Warning present |  | bool
00270.14 | [R] | PitWarn4.CableBreakFlowMonitorWarn |  | Dosing pump cable breakdown on Flow Monitor (Flow sensor sig. fault) | 0 = No Warning 1 = Warning present |  | bool
00270.15 | [R] | PitWarn4.CableBreakAnalogRefWarn |  | Dosing pump cable breakdown on Analogue (Reference input sig. fault) | 0 = No Warning 1 = Warning present |  | bool
00271 | [R] | GrinderOperatingMode |  | Grinder operating mode | 0 = Not present 1 = Out of operation 2 = Alarm 3 = Stopped 4 = Forward 5 = Reverse |  | enum
00391 | [R] | UserDigitalInBlock1 |  | User digital inputs 15-0 |  |  | unscaled
00392 | [R] | UserDigitalInBlock2 |  | User digital inputs 31-16 |  |  | unscaled
00393 | [R] | UserDigitalOutput |  | User digital outputs |  |  | unscaled
00394 | [R] | UserAnalogInput4 |  | User analog input 4 |  | 0.1 | %
00395 | [R] | UserAnalogInput5 |  | User analog input 5 |  | 0.1 | %
PIT DATA [R]
00301 | [R] | PitWaterLevel |  | Pit water level |  | 0.01 | m
00302 | [R] | PitSwitchWaterLevel |  | Pit water level (float switches) |  |  | unscaled
00303 | [R] | PitDepth |  | Depth of pit |  | 0.01 | m
00304 | [R] | PitFlowIn |  | Flow into the pit |  | 0.1 | l/s
00305 | [R] | PitAverageFlowIn |  | Average flow into the pit |  | 0.1 | l/s
00306 | [R] | PitFlowOut |  | Flow out of the pit |  | 0.1 | l/s
00307 | [R] | PitAverageFlowOut |  | Average flow out of the pit |  | 0.1 | l/s
00308 | [R] | PitPowerHI |  | Pit power consumption |  | 1 | W
00309 | [R] | PitPowerLO
00310 | [R] | PitEnergyHI |  | Pit energy consumption |  | 0.1 | kWh
00311 | [R] | PitEnergyLO
00312 | [R] | PitEnergyYesterday |  | Pit energy comsumption yesterday |  | 0.1 | kWh
00313 | [R] | PitEnergyToday |  | Pit energy comsumption today |  | 0.1 | kWh
00314 | [R] | PitSpecificEnergy |  | Pit specific energy consumption |  | 1 | Wh/m3
00315 | [R] | PitPumpedVolumeHI |  | Pit pumped volume |  | 0.1 | m3
00316 | [R] | PitPumpedVolumeLO |  |  |  |  | m3
00317 | [R] | PitPumpedVolumeYesterday |  | Pit pumped volume yesterday |  | 0.1 | m3
00318 | [R] | PitPumpedVolumeToday |  | Pit pumped volume today |  | 0.1 | m3
00319 | [R] | PitMixerAvgStartsPerHour |  | Average mixer starts per hour |  |  | unscaled
00320 | [R] | PitOverflowVolume |  | Overflow volume, 16 bit value |  | 0.1 | m3
00321 | [R] | PitOverflowVolumeYesterday |  | Overflow volume yesterday |  | 0.1 | m3
00322 | [R] | PitOverflowVolumeToday |  | Overflow volume today |  | 0.1 | m3
00323 | [R] | PitOverflowTime |  | Overflow time |  | 1 | min
00324 | [R] | PitOverflowTimeYesterday |  | Overflow time yesterday |  | 1 | min
00325 | [R] | PitOverflowTimeToday |  | Overflow time today |  | 1 | min
00326 | [R] | PitOverflowCounter |  | Number of overflows |  |  | unscaled
00327 | [R] | PitOverflowCounterYesterday |  | Number of overflows yesterday |  |  | unscaled
00328 | [R] | PitOverflowCounterToday |  | Number of overflows today |  |  | unscaled
00329 | [R] | PitOperatingTimeHI |  | Pit operating time |  | 1 | min
00330 | [R] | PitOperatingTimeLO
00331 | [R] | Pit2PumpsOprTimeHI |  | 2 pumps operating time |  | 1 | min
00332 | [R] | Pit2PumpsOprTimeLO |  |  |  |  | min
00333 | [R] | Pit2PumpsOprTimeYesterday |  | 2 pumps operating time yesterday |  | 1 | min
00334 | [R] | Pit2PumpsOprTimeToday |  | 2 pumps operating time today |  | 1 | min
00335 | [R] | Pit3PumpsOprTimeHI |  | 3 pumps operating time |  | 1 | min
00336 | [R] | Pit3PumpsOprTimeLO |  |  |  |  | min
00337 | [R] | Pit3PumpsOprTimeYesterday |  | 3 pumps operating time yesterday |  | 1 | min
00338 | [R] | Pit3PumpsOprTimeToday |  | 3 pumps operating time today |  | 1 | min
00339 | [R] | Pit4PumpsOprTimeHI |  | 4 pumps operating time |  | 1 | min
00340 | [R] | Pit4PumpsOprTimeLO |  |  |  |  | min
00341 | [R] | Pit4PumpsOprTimeYesterday |  | 4 pumps operating time yesterday |  | 1 | min
00342 | [R] | Pit4PumpsOprTimeToday |  | 4 pumps operating time today |  | 1 | min
00343 | [R] | Pit5PumpsOprTimeHI |  | 5 pumps operating time |  | 1 | min
00344 | [R] | Pit5PumpsOprTimeLO |  |  |  |  | min
00345 | [R] | Pit5PumpsOprTimeYesterday |  | 5 pumps operating time yesterday |  | 1 | min
00346 | [R] | Pit5PumpsOprTimeToday |  | 5 pumps operating time today |  | 1 | min
00347 | [R] | Pit6PumpsOprTimeHI |  | 6 pumps operating time |  | 1 | min
00348 | [R] | Pit6PumpsOprTimeLO |  |  |  |  | min
00349 | [R] | Pit6PumpsOprTimeYesterday |  | 6 pumps operating time yesterday |  | 1 | min
00350 | [R] | Pit6PumpsOprTimeToday |  | 6 pumps operating time today |  | 1 | min
00351 | [R] | UserAnalogInput1 |  | User analog input 1 |  | 0.1 | %
00352 | [R] | UserAnalogInput2 |  | User analog input 2 |  | 0.1 | %
00353 | [R] | UserAnalogInput3 |  | User analog input 3 |  | 0.1 | %
00354 | [R] | Pit0PumpsOprTimeHI |  | 0 pumps operating time |  | 1 | min
00355 | [R] | Pit0PumpsOprTimeLO
00356 | [R] | Pit0PumpsOprTimeYesterday |  | 0 pumps operating time yesterday |  | 1 | min
00357 | [R] | Pit0PumpsOprTimeToday |  | 0 pumps operating time today |  | 1 | min
00358 | [R] | Pit1PumpsOprTimeHI |  | 1 pump operating time |  | 1 | min
00359 | [R] | Pit1PumpsOprTimeLO
00360 | [R] | Pit1PumpsOprTimeYesterday |  | 1 pumps operating time yesterday |  | 1 | min
00361 | [R] | Pit1PumpsOprTimeToday |  | 1 pumps operating time today |  | 1 | min
00362 | [R] | MixerRuntime |  | Mixer runtime |  | 1 | min
00363 | [R] | MixerStartCounter |  | Mixer starts |  |  | unscaled
00364 | [R] | UserDefCounter1 |  | User defined counter 1 |  |  | unscaled
00365 | [R] | UserDefCounter2 |  | User defined counter 2 |  |  | unscaled
00366 | [R] | UserDefCounter3 |  | User defined counter 3 |  |  | unscaled
00367 | [R] | PitOutletPressure |  | Outlet (discharge) pressure of the pit |  | 0.001 | bar
00368 | [R] | PitOverflowVolume32bitHI |  | Pit Overflow Volume, 32 bit value |  | 0.1 | m3
00369 | [R] | PitOverflowVolume32bitLO
00370 | [R] | PitOverflowTime32bitHI |  | Overflow time, 32 bit value |  | 1 | min
00371 | [R] | PitOverflowTime32bitLO
00372 | [R] | UserDefCounter1Today |  | User defined counter 1 today |  |  | unscaled
00373 | [R] | UserDefCounter2Today |  | User defined counter 2 today |  |  | unscaled
00374 | [R] | UserDefCounter3Today |  | User defined counter 3 today |  |  | unscaled
00375 | [R] | UserDefCounter1Yesterday |  | User defined counter 1 Yesterday |  |  | unscaled
00376 | [R] | UserDefCounter2Yesterday |  | User defined counter 2 Yesterday |  |  | unscaled
00377 | [R] | UserDefCounter3Yesterday |  | User defined counter 3 Yesterday |  |  | unscaled
00378 | [R] | H2SLevelActual |  | Actual Hydrogen Sulfide (H2S) level |  | 1 | ppm
00379 | [R] | H2SLevelToday |  | Average Hydrogen Sulfide (H2S) level today |  | 1 | ppm
00380 | [R] | H2SLevelYesterday |  | Average Hydrogen Sulfide (H2S) level yesterday |  | 1 | ppm
00381 | [R] | DosingFeedTankLevel |  | Level in dosing feed tank |  | 0.01 | m
00382 | [R] | DosingVolumeTotalHI |  | Dosed precipitation chemical volume in total |  | 0.001 | m3
00383 | [R] | DosingVolumeTotalLO
00384 | [R] | DosingVolumeToday |  | Dosed precipitation chemical volume today |  | 0.001 | m3
00385 | [R] | DosingVolumeYesterday |  | Dosed precipitation chemical volume yesterday |  | 0.001 | m3
00386 | [R] | DosingRefActual |  | The actual chemical dosing reference (setpoint) |  | 0.1 | ltr/h
00387 | [R] | GrinderOperatingTimeHI |  | Grinder operating time |  | 1 | min
00388 | [R] | GrinderOperatingTimeLO
00389 | [R] | GrinderReverseCounterHI |  | Grinder reverse counter |  |  | unscaled
00390 | [R] | GrinderReverseCounterLO
00391 | [R] | UserDigitalInHI |  | User digital inputs 31-16 |  |  | unscaled
00392 | [R] | UserDigitalInLO |  | User digital inputs 15-0 |  |  | unscaled
00393 | [R] | UserDigitalOut |  | User digital outputs |  |  | unscaled
00393 | [R] | UserAnalogInput4 |  | User analog input 4 |  | 0.1 | %
00394 | [R] | UserAnalogInput5 |  | User analog input 5 |  | 0.1 | %
PUMP 1 [R]
00401.0 | [R] | Pump1Status.Presence |  | Presence of pump 1 | 0 = No present 1 = Present |  | bool
00401.1 | [R] | Pump1Status.Running |  | Rotation status of pump 1 | 0 = No rotation 1 = Rotation |  | bool
00401.2 | [R] | Pump1Status.MonitoringFault |  | Monitoring status of pump 1 | 0 = No fault 1 = Monitoring fault |  | bool
00401.3 | [R] | Pump1Status.Warning |  | Warning status of pump 1 | 0 = No warning 1 = Warning |  | bool
00401.4 | [R] | Pump1Status.Alarm |  | Alarm status of pump 1 | 0 = No alarm 1 = Alarm |  | bool
00401.5 | [R] | Pump1Status.IO11xPresent |  | IO 11x presence status | 0 = Not present 1 = Present |  | bool
00401.6 | [R] | Pump1Status.IO11xFault |  | IO 11x alarm status | 0 = No alarm 1 = Alarm |  | bool
00401.7 | [R] | Pump1Status.MP204Present |  | MP 204 presence status | 0 = Not present 1 = Present |  | bool
00401.8 | [R] | Pump1Status.MP204Fault |  | MP 204 alarm status | 0 = No alarm 1 = Alarm |  | bool
00401.9 | [R] | Pump1Status.CUEPresent |  | CUE presence status | 0 = Not present 1 = Present |  | bool
00401.10 | [R] | Pump1Status.CUEFault |  | CUE alarm status | 0 = No alarm 1 = Alarm |  | bool
00401.11 | [R] | Pump1Status.PumpDisabled |  | Enabled/Disabled status of pump 1 | 0 = Enabled 1 = Disabled |  | bool
00402 | [R] | Pump1ControlSource |  | Control source of pump 1 | 0 = Auto 1 = Manual by switch 2 = Manual by display 3 = Manual from bus 255 = - |  | enum
00403 | [R] | Pump1ConnectionType |  | Connection type of pump 1 | 0 = CU 36x relay 1 = IO 35x relay 2 = CU 36x+VFD 3 = IO 35x + VFD 255 = - |  | enum
00404 | [R] | Pump1OprTimeHI |  | Operating time of pump 1 |  | 1 | min
00405 | [R] | Pump1OprTimeLO
00406 | [R] | Pump1TimeToServiceHI |  | Time to service for pump 1 |  | 1 | min
00407 | [R] | Pump1TimeToServiceLO |  |  |  |  | min
00408 | [R] | Pump1OprTimeYesterday |  | Operating time yesterday, pump 1 |  | 1 | min
00409 | [R] | Pump1OprTimeToday |  | Operating time today, pump 1 |  | 1 | min
00410 | [R] | Pump1LatestOprTime |  | Latest operating time for pump 1 |  | 1 | s
00411 | [R] | Pump1StartCounterHI |  | Start counter for pump 1 |  |  | unscaled
00412 | [R] | Pump1StartCounterLO |  |  |  |  | unscaled
00413 | [R] | Pump1StartCounterYesterday |  | Start counter yesterday, pump 1 |  |  | unscaled
00414 | [R] | Pump1StartCounterToday |  | Start counter today, pump 1 |  |  | unscaled
00415 | [R] | Pump1AvgStartsPerHour |  | Average starts per hour for pump 1 |  |  | unscaled
00416 | [R] | Pump1Flow |  | Flow, pump 1 |  | 0.1 | l/s
00417 | [R] | Pump1LatestFlow |  | Latest flow, pump 1 |  | 0.1 | l/s
00418 | [R] | Pump1Current |  | Motor current, pump 1 |  | 0.1 | A
00419 | [R] | Pump1LatestCurrent |  | Latest motor current, pump 1 |  | 0.1 | A
00420 | [R] | Pump1Voltage |  | Motor voltage, pump 1 |  | 0.1 | V
00421 | [R] | Pump1Insulation |  | Motor insulation resistance, pump 1 |  | 10 | kOhm
00422 | [R] | Pump1WaterInOil |  | Water in oil measurement, pump 1 |  | 0.1 | %
00423.0 | [R] | Pump1Alarms1.MotorTemp.alarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No alarm 1 = Alarm |  | bool
00423.1 | [R] | Pump1Alarms1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No alarm 1 = Alarm |  | bool
00423.2 | [R] | Pump1Alarms1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No alarm 1 = Alarm |  | bool
00423.3 | [R] | Pump1Alarms1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No alarm 1 = Alarm |  | bool
00423.4 | [R] | Pump1Alarms1.MotorSupportBearingTemp.High |  | Motor support bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00423.5 | [R] | Pump1Alarms1.MotorMainBearingTemp.High |  | Motor bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00423.6 | [R] | Pump1Alarms1.MotorInsulationRes.Low |  | Motor insulation resistance low | 0 = No alarm 1 = Alarm |  | bool
00423.7 | [R] | Pump1Alarms1.MotorLowVoltage |  | Motor voltage low | 0 = No alarm 1 = Alarm |  | bool
00423.8 | [R] | Pump1Alarms1.MotorHighVoltage |  | Motor voltage high | 0 = No alarm 1 = Alarm |  | bool
00423.9 | [R] | Pump1Alarms1.MotorPhaseSequenceReversal |  | Motor phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00423.10 | [R] | Pump1Alarms1.MotorOverload |  | Motor overload | 0 = No alarm 1 = Alarm |  | bool
00423.11 | [R] | Pump1Alarms1.MotorUnderload |  | Motor underload | 0 = No alarm 1 = Alarm |  | bool
00423.12 | [R] | Pump1Alarms1.MotorProtectorTestTrip |  | Motor protector test trip | 0 = No alarm 1 = Alarm |  | bool
00423.13 | [R] | Pump1Alarms1.MotorMissingPhase |  | Motor missing phase | 0 = No alarm 1 = Alarm |  | bool
00423.14 | [R] | Pump1Alarms1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No alarm 1 = Alarm |  | bool
00423.15 | [R] | Pump1Alarms1.LoadContinuesDespiteMotorRelayisOff |  | Load continues, but motor relay is off | 0 = No alarm 1 = Alarm |  | bool
00424.0 | [R] | Pump1Alarms2.MotorProtectorActivated |  | Motor protector activated | 0 = No alarm 1 = Alarm |  | bool
00424.1 | [R] | Pump1Alarms2.MotorPhaseFailure |  | Motor phase failure | 0 = No alarm 1 = Alarm |  | bool
00424.2 | [R] | Pump1Alarms2.MotorMoistureSwitch |  | Motor moisture | 0 = No alarm 1 = Alarm |  | bool
00424.3 | [R] | Pump1Alarms2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No alarm 1 = Alarm |  | bool
00424.4 | [R] | Pump1Alarms2.WaterInOilLevelTooHigh |  | Water in oil level too high | 0 = No alarm 1 = Alarm |  | bool
00424.5 | [R] | Pump1Alarms2.MotorFaultInMainsSupply |  | Fault in the mains power supply | 0 = No alarm 1 = Alarm |  | bool
00424.6 | [R] | Pump1Alarms2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No alarm 1 = Alarm |  | bool
00424.7 | [R] | Pump1Alarms2.MotorMaxStartsPerHourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00424.8 | [R] | Pump1Alarms2.MotorOperatingTimeServiceLimitExceeded |  | Motor service time exceeded | 0 = No alarm 1 = Alarm |  | bool
00424.9 | [R] | Pump1Alarms2.TooManyPumpAuto-restarts |  | Too many auto restarts of pump | 0 = No alarm 1 = Alarm |  | bool
00424.10 | [R] | Pump1Alarms2.PumpLowFlow |  | Pump low flow | 0 = No alarm 1 = Alarm |  | bool
00424.11 | [R] | Pump1Alarms2.PumpMaxContinuousRun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00424.12 | [R] | Pump1Alarms2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No alarm 1 = Alarm |  | bool
00424.13 | [R] | Pump1Alarms2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No alarm 1 = Alarm |  | bool
00424.14 | [R] | Pump1Alarms2.ParameterVerificatonErrEEPROM |  | EEPROM error in parameter area (85) PLACE HOLDER) | 0 = No alarm 1 = Alarm |  | bool
00424.15 | [R] | Pump1Alarms2.DriveProtectMeasFault |  | Motor drive protection measurement fault (PLACE HOLDER) | 0 = No alarm 1 = Alarm |  | bool
00425.0 | [R] | Pump1.Alarms3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No alarm 1 = Alarm |  | bool
00425.1 | [R] | Pump1.Alarms3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No alarm 1 = Alarm |  | bool
00425.2 | [R] | Pump1.Alarms3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No alarm 1 = Alarm |  | bool
00425.3 | [R] | Pump1.Alarms3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No alarm 1 = Alarm |  | bool
00425.4 | [R] | Pump1.Alarms3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No alarm 1 = Alarm |  | bool
00425.5 | [R] | Pump1.Alarms3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No alarm 1 = Alarm |  | bool
00425.6 | [R] | Pump1.Alarms3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00425.7 | [R] | Pump1.Alarms3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00425.8 | [R] | Pump1.Alarms3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No alarm 1 = Alarm |  | bool
00425.9 | [R] | Pump1.Alarms3.SetupConflict |  | Conflict in setup parameters | 0 = No alarm 1 = Alarm |  | bool
00425.10 | [R] | Pump1.Alarms3.GeneralHardwareFault |  | General hardware fault | 0 = No alarm 1 = Alarm |  | bool
00425.11 | [R] | Pump1.Alarms3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No alarm 1 = Alarm |  | bool
00425.12 | [R] | Pump1.Alarms3.InrushFault |  | Inrush fault | 0 = No alarm 1 = Alarm |  | bool
00425.13 | [R] | Pump1.Alarms3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No alarm 1 = Alarm |  | bool
00425.14 | [R] | Pump1.Alarms3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00425.15 | [R] | Pump1.Alarms3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00426.0 | [R] | Pump1Warnings1.MotorTemp.AlarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No warning 1 = Warning |  | bool
00426.1 | [R] | Pump1Warnings1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No warning 1 = Warning |  | bool
00426.2 | [R] | Pump1Warnings1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No warning 1 = Warning |  | bool
00426.3 | [R] | Pump1Warnings1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No warning 1 = Warning |  | bool
00426.4 | [R] | Pump1Warnings1.MotorsupportbearingTemp.High |  | Motor support bearing temperature high | 0 = No warning 1 = Warning |  | bool
00426.5 | [R] | Pump1Warnings1.MotormainbearingTemp.High |  | Motor bearing temperature high | 0 = No warning 1 = Warning |  | bool
00426.6 | [R] | Pump1Warnings1.Motorinsulationres.Low |  | Motor insulation resistance low | 0 = No warning 1 = Warning |  | bool
00426.7 | [R] | Pump1Warnings1.MotorLowVoltage |  | Motor voltage low | 0 = No warning 1 = Warning |  | bool
00426.8 | [R] | Pump1Warnings1.MotorHighVoltage |  | Motor voltage high | 0 = No warning 1 = Warning |  | bool
00426.9 | [R] | Pump1Warnings1.MotorPhasesequencereversal |  | Motor phase sequence reversed | 0 = No warning 1 = Warning |  | bool
00426.10 | [R] | Pump1Warnings1.Motoroverload |  | Motor overload | 0 = No warning 1 = Warning |  | bool
00426.11 | [R] | Pump1Warnings1.Motorunderload |  | Motor underload | 0 = No warning 1 = Warning |  | bool
00426.12 | [R] | Pump1Warnings1.Motorprotectortesttrip |  | Motor protector test trip | 0 = No warning 1 = Warning |  | bool
00426.13 | [R] | Pump1Warnings1.MotormissingPhase |  | Motor missing phase | 0 = No warning 1 = Warning |  | bool
00426.14 | [R] | Pump1Warnings1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No warning 1 = Warning |  | bool
00426.15 | [R] | Pump1Warnings1.LoadContinuesDespiteMotorRelayIsOff |  | Load continues, but motor relay is off | 0 = No warning 1 = Warning |  | bool
00427.0 | [R] | Pump1Warnings2.MotorProtectorActivated |  | Motor protector activated | 0 = No warning 1 = Warning |  | bool
00427.1 | [R] | Pump1Warnings2.MotorPhaseFailure |  | Motor phase failure | 0 = No warning 1 = Warning |  | bool
00427.2 | [R] | Pump1Warnings2.MotorMoistureSwitch |  | Motor moisture | 0 = No warning 1 = Warning |  | bool
00427.3 | [R] | Pump1Warnings2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No warning 1 = Warning |  | bool
00427.4 | [R] | Pump1Warnings2.WaterinoilLevelTooHigh |  | Water in oil level too high | 0 = No warning 1 = Warning |  | bool
00427.5 | [R] | Pump1Warnings2.MotorFaultinmainssupply |  | Fault in the mains power supply | 0 = No warning 1 = Warning |  | bool
00427.6 | [R] | Pump1Warnings2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No warning 1 = Warning |  | bool
00427.7 | [R] | Pump1Warnings2.MotorMaxstartsperhourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No warning 1 = Warning |  | bool
00427.8 | [R] | Pump1Warnings2.MotoroperatingtimeserviceLimitExceeded |  | Motor service time exceeded | 0 = No warning 1 = Warning |  | bool
00427.9 | [R] | Pump1Warnings2.TooManyPumpauto-restarts |  | Too many auto restarts of pump | 0 = No warning 1 = Warning |  | bool
00427.10 | [R] | Pump1Warnings2.PumpLowFlow |  | Pump low flow | 0 = No warning 1 = Warning |  | bool
00427.11 | [R] | Pump1Warnings2.PumpMaxcontinuousrun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No warning 1 = Warning |  | bool
00427.12 | [R] | Pump1Warnings2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No warning 1 = Warning |  | bool
00427.13 | [R] | Pump1Warnings2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No warning 1 = Warning |  | bool
00427.14 | [R] | Pump1Warnings2.ParameterVerificatonErrEEPROM |  | EEPROM error in parameter area (85) PLACE HOLDER) | 0 = No warning 1 = Warning |  | bool
00427.15 | [R] | Pump1Warnings2.DriveProtectMeasFault |  | Motor drive protection measurement fault (PLACE HOLDER) | 0 = No warning 1 = Warning |  | bool
00428.0 | [R] | Pump1.Warnings3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No warning 1 = Warning |  | bool
00428.1 | [R] | Pump1.Warnings3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No warning 1 = Warning |  | bool
00428.2 | [R] | Pump1.Warnings3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No warning 1 = Warning |  | bool
00428.3 | [R] | Pump1.Warnings3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No warning 1 = Warning |  | bool
00428.4 | [R] | Pump1.Warnings3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No warning 1 = Warning |  | bool
00428.5 | [R] | Pump1.Warnings3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No warning 1 = Warning |  | bool
00428.6 | [R] | Pump1.Warnings3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00428.7 | [R] | Pump1.Warnings3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00428.8 | [R] | Pump1.Warnings3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No warning 1 = Warning |  | bool
00428.9 | [R] | Pump1.Warnings3.SetupConflict |  | Conflict in setup parameters | 0 = No warning 1 = Warning |  | bool
00428.10 | [R] | Pump1.Warnings3.GeneralhardwareFault |  | General hardware fault | 0 = No warning 1 = Warning |  | bool
00428.11 | [R] | Pump1.Warnings3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No warning 1 = Warning |  | bool
00428.12 | [R] | Pump1.Warnings3.InrushFault |  | Inrush fault | 0 = No warning 1 = Warning |  | bool
00428.13 | [R] | Pump1.Warnings3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No warning 1 = Warning |  | bool
00428.14 | [R] | Pump1.Warnings3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No warning 1 = Warning |  | bool
00428.15 | [R] | Pump1.Warnings3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No warning 1 = Warning |  | bool
00429 | [R] | Pump1MotorTemperature1 |  | Motor temperature 1, pump 1 |  | 1 | C
00430 | [R] | Pump1MotorTemperature2 |  | Motor temperature 2, pump 1 |  | 1 | C
00431 | [R] | Pump1PowerHI |  | Power consumption, pump 1 |  | 1 | W
00432 | [R] | Pump1PowerLO
00433 | [R] | Pump1EnergyHI |  | Energy consumption, pump 1 |  | 0.1 | kWh
00434 | [R] | Pump1EnergyLO
00435 | [R] | Pump1CosPhi |  | Motor cosine phi, pump 1 |  | 0.01
00436 | [R] | Pump1Frequency |  | Motor applied frequency, pump 1 |  | 0.01 | Hz
00437 | [R] | Pump1VFDmode |  | Mode of variable frequency drive | 0 = Not in control 1 = - 2 = Stopped 3 = Reversed flushing 4 = Start flushing 5 = Normal 6 = Run flushing 255 = - |  | enum
00438 | [R] | Pump1Torque |  | Motor torque, pump 1 |  | 0.1 | Nm
00439 | [R] | Pump1iAsym |  | Line current asymmetry, pump 1 |  | 0.1 | %
00440.0 | [R] | Pump1Sensors.WIO |  | Water-In-Oil sensor | 0 = Not present 1 = Sensor present |  | bool
00440.1 | [R] | Pump1Sensors.Current |  | Motor current sensor | 0 = Not present 1 = Sensor present |  | bool
00441.0 | [R] | Pump1Alarms4.LeakageCurrent |  | Leakage current | 0 = No alarm 1 = Alarm |  | bool
00441.1 | [R] | Pump1Alarms4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No alarm 1 = Alarm |  | bool
00441.2 | [R] | Pump1Alarms4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00441.3 | [R] | Pump1Alarms4.Overcurrent |  | Overcurrent | 0 = No alarm 1 = Alarm |  | bool
00441.4 | [R] | Pump1Alarms4.MotorProtectionActivated |  | Motor protection activated | 0 = No alarm 1 = Alarm |  | bool
00441.5 | [R] | Pump1Alarms4.ChangeBearings |  | Change bearings | 0 = No alarm 1 = Alarm |  | bool
00441.6 | [R] | Pump1Alarms4.LubricateBearings |  | Lubricate bearings | 0 = No alarm 1 = Alarm |  | bool
00441.7 | [R] | Pump1Alarms4.MotorRecognitionFailed |  | Motor not recognized | 0 = No alarm 1 = Alarm |  | bool
00441.8 | [R] | Pump1Alarms4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No alarm 1 = Alarm |  | bool
00441.9 | [R] | Pump1Alarms4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00441.10 | [R] | Pump1Alarms4.DryRunning |  | Dry running | 0 = No alarm 1 = Alarm |  | bool
00441.11 | [R] | Pump1Alarms4.VFDnotReady |  | Variable frequency drive not ready | 0 = No alarm 1 = Alarm |  | bool
00441.12 | [R] | Pump1Alarms4.Other |  | Other | 0 = No alarm 1 = Alarm |  | bool
00441.13 | [R] | Pump1Alarms4.PumpBlocked |  | Pump blocked alarm | 0 = No alarm 1 = Alarm |  | bool
00441.14 | [R] | Pump1Alarms4.SignalFaultPowerSensor |  | Power sensor signal fault alarm | 0 = No alarm 1 = Alarm |  | bool
00442.0 | [R] | Pump1Warnings4.LeakageCurrent |  | Leakage current | 0 = No warning 1 = Warning |  | bool
00442.1 | [R] | Pump1Warnings4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No warning 1 = Warning |  | bool
00442.2 | [R] | Pump1Warnings4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00442.3 | [R] | Pump1Warnings4.Overcurrent |  | Overcurrent | 0 = No warning 1 = Warning |  | bool
00442.4 | [R] | Pump1Warnings4.MotorProtectionActivated |  | Motor protection activated | 0 = No warning 1 = Warning |  | bool
00442.5 | [R] | Pump1Warnings4.ChangeBearings |  | Change bearings | 0 = No warning 1 = Warning |  | bool
00442.6 | [R] | Pump1Warnings4.LubricateBearings |  | Lubricate bearings | 0 = No warning 1 = Warning |  | bool
00442.7 | [R] | Pump1Warnings4.MotorRecognitionFailed |  | Motor not recognized | 0 = No warning 1 = Warning |  | bool
00442.8 | [R] | Pump1Warnings4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No warning 1 = Warning |  | bool
00442.9 | [R] | Pump1Warnings4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00442.10 | [R] | Pump1Warnings4.DryRunning |  | Dry running | 0 = No warning 1 = Warning |  | bool
00442.11 | [R] | Pump1Warnings4.VFDnotReady |  | Variable frequency drive not ready | 0 = No warning 1 = Warning |  | bool
00442.12 | [R] | Pump1Warnings4.Other |  | Other | 0 = No warning 1 = Warning |  | bool
00442.13 | [R] | Pump1Warnings4.PumpBlocked |  | Pump blocked warning | 0 = No alarm 1 = Warning |  | bool
00442.14 | [R] | Pump1Warnings4.SignalFaultPowerSensor |  | Power sensor signal fault warning | 0 = No alarm 1 = Warning |  | bool
00443 | [R] | Pump1AntiBlockingCounter |  | Number of anti blockings in the pump |  |  | unscaled
00444 | [R] | Pump1AISetpointSelect |  | Analog input used as setpoint for pump 1 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00445 | [R] | Pump1SetpointType |  | Setpoint type for pump 1 | 0 = Fixed value 1 = Analog input |  | enum
00446 | [R] | Pump1FeedbackSensorType |  | Feedback sensor type for pump 1 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00447 | [R] | Pump1ControlMode |  | Control mode for pump 1 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00448 | [R] | Pump1ActualSetpoint |  | Actual setpoint for pump 1 |  | 1 | %
00449 | [R] | Pump1FixedFrequency |  | Fixed frequency for pump 1 |  | 0.01 | Hz
PUMP 2 [R]
00451.0 | [R] | Pump2Status.Presence |  | Presence of pump 2 | 0 = No present 1 = Present |  | bool
00451.1 | [R] | Pump2Status.Running |  | Rotation status of pump 2 | 0 = No rotation 1 = Rotation |  | bool
00451.2 | [R] | Pump2Status.MonitoringFault |  | Monitoring status of pump 2 | 0 = No fault 1 = Monitoring fault |  | bool
00451.3 | [R] | Pump2Status.Warning |  | Warning status of pump 2 | 0 = No warning 1 = Warning |  | bool
00451.4 | [R] | Pump2Status.Alarm |  | Alarm status of pump 2 | 0 = No alarm 1 = Alarm |  | bool
00451.5 | [R] | Pump2Status.IO11xPresent |  | IO 11x presence status | 0 = Not present 1 = Present |  | bool
00451.6 | [R] | Pump2Status.IO11xFault |  | IO 11x alarm status | 0 = No alarm 1 = Alarm |  | bool
00451.7 | [R] | Pump2Status.MP204Present |  | MP 204 presence status | 0 = Not present 1 = Present |  | bool
00451.8 | [R] | Pump2Status.MP204Fault |  | MP 204 alarm status | 0 = No alarm 1 = Alarm |  | bool
00451.9 | [R] | Pump2Status.CUEPresent |  | CUE presence status | 0 = Not present 1 = Present |  | bool
00451.10 | [R] | Pump2Status.CUEFault |  | CUE alarm status | 0 = No alarm 1 = Alarm |  | bool
00451.11 | [R] | Pump2Status.PumpDisabled |  | Enabled/Disabled status of pump 2 | 0 = Enabled 1 = Disabled |  | bool
00452 | [R] | Pump2ControlSource |  | Control source of pump 2 | 0 = Auto 1 = Manual by switch 2 = Manual by display 3 = Manual from bus 255 = - |  | enum
00453 | [R] | Pump2ConnectionType |  | Connection type of pump 2 | 0 = CU 36x relay 1 = IO 35x relay 2 = CU 36x+VFD 3 = IO 35x + VFD 255 = - |  | enum
00454 | [R] | Pump2OprTimeHI |  | Operating time of pump 2 |  | 1 | min
00455 | [R] | Pump2OprTimeLO
00456 | [R] | Pump2TimeToServiceHI |  | Time to service for pump 2 |  | 1 | min
00457 | [R] | Pump2TimeToServiceLO
00458 | [R] | Pump2OprTimeYesterday |  | Operating time yesterday, pump 2 |  | 1 | min
00459 | [R] | Pump2OprTimeToday |  | Operating time today, pump 2 |  | 1 | min
00460 | [R] | Pump2LatestOprTime |  | Latest operating time for pump 2 |  | 1 | s
00461 | [R] | Pump2StartCounterHI |  | Start counter for pump 2 |  |  | unscaled
00462 | [R] | Pump2StartCounterLO
00463 | [R] | Pump2StartCounterYesterday |  | Start counter yesterday, pump 2 |  |  | unscaled
00464 | [R] | Pump2StartCounterToday |  | Start counter today, pump 2 |  |  | unscaled
00465 | [R] | Pump2AvgStartsPerHour |  | Average starts per hour for pump 2 |  |  | unscaled
00466 | [R] | Pump2Flow |  | Flow, pump 2 |  | 0.1 | l/s
00467 | [R] | Pump2LatestFlow |  | Latest flow, pump 2 |  | 0.1 | l/s
00468 | [R] | Pump2Current |  | Motor current, pump 2 |  | 0.1 | A
00469 | [R] | Pump2LatestCurrent |  | Latest motor current, pump 2 |  | 0.1 | A
00470 | [R] | Pump2Voltage |  | Motor voltage, pump 2 |  | 0.1 | V
00471 | [R] | Pump2Insulation |  | Motor insulation resistance, pump 2 |  | 10 | kOhm
00472 | [R] | Pump2WaterInOil |  | Water in oil measurement, pump 2 |  | 0.1 | %
00473.0 | [R] | Pump2Alarms1.MotorTemp.alarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No alarm 1 = Alarm |  | bool
00473.1 | [R] | Pump2Alarms1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No alarm 1 = Alarm |  | bool
00473.2 | [R] | Pump2Alarms1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No alarm 1 = Alarm |  | bool
00473.3 | [R] | Pump2Alarms1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No alarm 1 = Alarm |  | bool
00473.4 | [R] | Pump2Alarms1.MotorSupportBearingTemp.High |  | Motor support bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00473.5 | [R] | Pump2Alarms1.MotorMainBearingTemp.High |  | Motor bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00473.6 | [R] | Pump2Alarms1.MotorInsulationRes.Low |  | Motor insulation resistance low | 0 = No alarm 1 = Alarm |  | bool
00473.7 | [R] | Pump2Alarms1.MotorLowVoltage |  | Motor voltage low | 0 = No alarm 1 = Alarm |  | bool
00473.8 | [R] | Pump2Alarms1.MotorHighVoltage |  | Motor voltage high | 0 = No alarm 1 = Alarm |  | bool
00473.9 | [R] | Pump2Alarms1.MotorPhaseSequenceReversal |  | Motor phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00473.10 | [R] | Pump2Alarms1.MotorOverload |  | Motor overload | 0 = No alarm 1 = Alarm |  | bool
00473.11 | [R] | Pump2Alarms1.MotorUnderload |  | Motor underload | 0 = No alarm 1 = Alarm |  | bool
00473.12 | [R] | Pump2Alarms1.MotorProtectorTestTrip |  | Motor protector test trip | 0 = No alarm 1 = Alarm |  | bool
00473.13 | [R] | Pump2Alarms1.MotorMissingPhase |  | Motor missing phase | 0 = No alarm 1 = Alarm |  | bool
00473.14 | [R] | Pump2Alarms1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No alarm 1 = Alarm |  | bool
00473.15 | [R] | Pump2Alarms1.LoadContinuesDespiteMotorRelayisOff |  | Load continues, but motor relay is off | 0 = No alarm 1 = Alarm |  | bool
00474.0 | [R] | Pump2Alarms2.MotorProtectorActivated |  | Motor protector activated | 0 = No alarm 1 = Alarm |  | bool
00474.1 | [R] | Pump2Alarms2.MotorPhaseFailure |  | Motor phase failure | 0 = No alarm 1 = Alarm |  | bool
00474.2 | [R] | Pump2Alarms2.MotorMoistureSwitch |  | Motor moisture | 0 = No alarm 1 = Alarm |  | bool
00474.3 | [R] | Pump2Alarms2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No alarm 1 = Alarm |  | bool
00474.4 | [R] | Pump2Alarms2.WaterInOilLevelTooHigh |  | Water in oil level too high | 0 = No alarm 1 = Alarm |  | bool
00474.5 | [R] | Pump2Alarms2.MotorFaultInMainsSupply |  | Fault in the mains power supply | 0 = No alarm 1 = Alarm |  | bool
00474.6 | [R] | Pump2Alarms2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No alarm 1 = Alarm |  | bool
00474.7 | [R] | Pump2Alarms2.MotorMaxStartsPerHourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00474.8 | [R] | Pump2Alarms2.MotorOperatingTimeServiceLimitExceeded |  | Motor service time exceeded | 0 = No alarm 1 = Alarm |  | bool
00474.9 | [R] | Pump2Alarms2.TooManyPumpAuto-restarts |  | Too many auto restarts of pump | 0 = No alarm 1 = Alarm |  | bool
00474.10 | [R] | Pump2Alarms2.PumpLowFlow |  | Pump low flow | 0 = No alarm 1 = Alarm |  | bool
00474.11 | [R] | Pump2Alarms2.PumpMaxContinuousRun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00474.12 | [R] | Pump2Alarms2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No alarm 1 = Alarm |  | bool
00474.13 | [R] | Pump2Alarms2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No alarm 1 = Alarm |  | bool
00474.14 | [R] | Pump2Alarms2.ParameterVerificatonErrEEPROM |  | EEPROM error in parameter area (85) PLACE HOLDER) | 0 = No alarm 1 = Alarm |  | bool
00474.15 | [R] | Pump2Alarms2.DriveProtectMeasFault |  | Motor drive protection measurement fault (PLACE HOLDER) | 0 = No alarm 1 = Alarm |  | bool
00475.0 | [R] | Pump2.Alarms3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No alarm 1 = Alarm |  | bool
00475.1 | [R] | Pump2.Alarms3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No alarm 1 = Alarm |  | bool
00475.2 | [R] | Pump2.Alarms3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No alarm 1 = Alarm |  | bool
00475.3 | [R] | Pump2.Alarms3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No alarm 1 = Alarm |  | bool
00475.4 | [R] | Pump2.Alarms3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No alarm 1 = Alarm |  | bool
00475.5 | [R] | Pump2.Alarms3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No alarm 1 = Alarm |  | bool
00475.6 | [R] | Pump2.Alarms3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00475.7 | [R] | Pump2.Alarms3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00475.8 | [R] | Pump2.Alarms3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No alarm 1 = Alarm |  | bool
00475.9 | [R] | Pump2.Alarms3.SetupConflict |  | Conflict in setup parameters | 0 = No alarm 1 = Alarm |  | bool
00475.10 | [R] | Pump2.Alarms3.GeneralHardwareFault |  | General hardware fault | 0 = No alarm 1 = Alarm |  | bool
00475.11 | [R] | Pump2.Alarms3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No alarm 1 = Alarm |  | bool
00475.12 | [R] | Pump2.Alarms3.InrushFault |  | Inrush fault | 0 = No alarm 1 = Alarm |  | bool
00475.13 | [R] | Pump2.Alarms3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No alarm 1 = Alarm |  | bool
00475.14 | [R] | Pump2.Alarms3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00475.15 | [R] | Pump2.Alarms3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00476.0 | [R] | Pump2Warnings1.MotorTemp.AlarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No warning 1 = Warning |  | bool
00476.1 | [R] | Pump2Warnings1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No warning 1 = Warning |  | bool
00476.2 | [R] | Pump2Warnings1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No warning 1 = Warning |  | bool
00476.3 | [R] | Pump2Warnings1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No warning 1 = Warning |  | bool
00476.4 | [R] | Pump2Warnings1.MotorsupportbearingTemp.High |  | Motor support bearing temperature high | 0 = No warning 1 = Warning |  | bool
00476.5 | [R] | Pump2Warnings1.MotormainbearingTemp.High |  | Motor bearing temperature high | 0 = No warning 1 = Warning |  | bool
00476.6 | [R] | Pump2Warnings1.Motorinsulationres.Low |  | Motor insulation resistance low | 0 = No warning 1 = Warning |  | bool
00476.7 | [R] | Pump2Warnings1.MotorLowVoltage |  | Motor voltage low | 0 = No warning 1 = Warning |  | bool
00476.8 | [R] | Pump2Warnings1.MotorHighVoltage |  | Motor voltage high | 0 = No warning 1 = Warning |  | bool
00476.9 | [R] | Pump2Warnings1.MotorPhasesequencereversal |  | Motor phase sequence reversed | 0 = No warning 1 = Warning |  | bool
00476.10 | [R] | Pump2Warnings1.Motoroverload |  | Motor overload | 0 = No warning 1 = Warning |  | bool
00476.11 | [R] | Pump2Warnings1.Motorunderload |  | Motor underload | 0 = No warning 1 = Warning |  | bool
00476.12 | [R] | Pump2Warnings1.Motorprotectortesttrip |  | Motor protector test trip | 0 = No warning 1 = Warning |  | bool
00476.13 | [R] | Pump2Warnings1.MotormissingPhase |  | Motor missing phase | 0 = No warning 1 = Warning |  | bool
00476.14 | [R] | Pump2Warnings1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No warning 1 = Warning |  | bool
00476.15 | [R] | Pump2Warnings1.LoadContinuesDespiteMotorRelayIsOff |  | Load continues, but motor relay is off | 0 = No warning 1 = Warning |  | bool
00477.0 | [R] | Pump2Warnings2.MotorProtectorActivated |  | Motor protector activated | 0 = No warning 1 = Warning |  | bool
00477.1 | [R] | Pump2Warnings2.MotorPhaseFailure |  | Motor phase failure | 0 = No warning 1 = Warning |  | bool
00477.2 | [R] | Pump2Warnings2.MotorMoistureSwitch |  | Motor moisture | 0 = No warning 1 = Warning |  | bool
00477.3 | [R] | Pump2Warnings2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No warning 1 = Warning |  | bool
00477.4 | [R] | Pump2Warnings2.WaterinoilLevelTooHigh |  | Water in oil level too high | 0 = No warning 1 = Warning |  | bool
00477.5 | [R] | Pump2Warnings2.MotorFaultinmainssupply |  | Fault in the mains power supply | 0 = No warning 1 = Warning |  | bool
00477.6 | [R] | Pump2Warnings2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No warning 1 = Warning |  | bool
00477.7 | [R] | Pump2Warnings2.MotorMaxstartsperhourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No warning 1 = Warning |  | bool
00477.8 | [R] | Pump2Warnings2.MotoroperatingtimeserviceLimitExceeded |  | Motor service time exceeded | 0 = No warning 1 = Warning |  | bool
00477.9 | [R] | Pump2Warnings2.TooManyPumpauto-restarts |  | Too many auto restarts of pump | 0 = No warning 1 = Warning |  | bool
00477.10 | [R] | Pump2Warnings2.PumpLowFlow |  | Pump low flow | 0 = No warning 1 = Warning |  | bool
00477.11 | [R] | Pump2Warnings2.PumpMaxcontinuousrun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No warning 1 = Warning |  | bool
00477.12 | [R] | Pump2Warnings2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No warning 1 = Warning |  | bool
00477.13 | [R] | Pump2Warnings2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No warning 1 = Warning |  | bool
00477.14 | [R] | Pump2Warnings2.ParameterVerificatonErrEEPROM |  | EEPROM error in parameter area (85) PLACE HOLDER) | 0 = No warning 1 = Warning |  | bool
00477.15 | [R] | Pump2Warnings2.DriveProtectMeasFault |  | Motor drive protection measurement fault (PLACE HOLDER) | 0 = No warning 1 = Warning |  | bool
00478.0 | [R] | Pump2.Warnings3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No warning 1 = Warning |  | bool
00478.1 | [R] | Pump2.Warnings3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No warning 1 = Warning |  | bool
00478.2 | [R] | Pump2.Warnings3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No warning 1 = Warning |  | bool
00478.3 | [R] | Pump2.Warnings3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No warning 1 = Warning |  | bool
00478.4 | [R] | Pump2.Warnings3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No warning 1 = Warning |  | bool
00478.5 | [R] | Pump2.Warnings3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No warning 1 = Warning |  | bool
00478.6 | [R] | Pump2.Warnings3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00478.7 | [R] | Pump2.Warnings3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00478.8 | [R] | Pump2.Warnings3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No warning 1 = Warning |  | bool
00478.9 | [R] | Pump2.Warnings3.SetupConflict |  | Conflict in setup parameters | 0 = No warning 1 = Warning |  | bool
00478.10 | [R] | Pump2.Warnings3.GeneralhardwareFault |  | General hardware fault | 0 = No warning 1 = Warning |  | bool
00478.11 | [R] | Pump2.Warnings3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No warning 1 = Warning |  | bool
00478.12 | [R] | Pump2.Warnings3.InrushFault |  | Inrush fault | 0 = No warning 1 = Warning |  | bool
00478.13 | [R] | Pump2.Warnings3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No warning 1 = Warning |  | bool
00478.14 | [R] | Pump2.Warnings3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No warning 1 = Warning |  | bool
00478.15 | [R] | Pump2.Warnings3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No warning 1 = Warning |  | bool
00479 | [R] | Pump2MotorTemperature1 |  | Motor temperature 1, pump 2 |  | 1 | C
00480 | [R] | Pump2MotorTemperature2 |  | Motor temperature 2, pump 2 |  | 1 | C
00481 | [R] | Pump2PowerHI |  | Power consumption, pump 2 |  | 1 | W
00482 | [R] | Pump2PowerLO
00483 | [R] | Pump2EnergyHI |  | Energy consumption, pump 2 |  | 0.1 | kWh
00484 | [R] | Pump2EnergyLO
00485 | [R] | Pump2CosPhi |  | Motor cosine phi, pump 2 |  | 0.01
00486 | [R] | Pump2Frequency |  | Motor applied frequency, pump 2 |  | 0.01 | Hz
00487 | [R] | Pump2VFDmode |  | Mode of variable frequency drive | 0 = Not in control 1 = - 2 = Stopped 3 = Reversed flushing 4 = Start flushing 5 = Normal 6 = Run flushing 255 = - |  | enum
00488 | [R] | Pump2Torque |  | Motor torque, pump 2 |  | 0.1 | Nm
00489 | [R] | Pump2iAsym |  | Line current asymmetry, pump 2 |  | 0.1 | %
00490.0 | [R] | Pump2Sensors.WIO |  | Water-In-Oil sensor | 0 = Not present 1 = Sensor present |  | bool
00490.1 | [R] | Pump2Sensors.Current |  | Motor current sensor | 0 = Not present 1 = Sensor present |  | bool
00491.0 | [R] | Pump2Alarms4.LeakageCurrent |  | Leakage current | 0 = No alarm 1 = Alarm |  | bool
00491.1 | [R] | Pump2Alarms4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No alarm 1 = Alarm |  | bool
00491.2 | [R] | Pump2Alarms4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00491.3 | [R] | Pump2Alarms4.Overcurrent |  | Overcurrent | 0 = No alarm 1 = Alarm |  | bool
00491.4 | [R] | Pump2Alarms4.MotorProtectionActivated |  | Motor protection activated | 0 = No alarm 1 = Alarm |  | bool
00491.5 | [R] | Pump2Alarms4.ChangeBearings |  | Change bearings | 0 = No alarm 1 = Alarm |  | bool
00491.6 | [R] | Pump2Alarms4.LubricateBearings |  | Lubricate bearings | 0 = No alarm 1 = Alarm |  | bool
00491.7 | [R] | Pump2Alarms4.MotorRecognitionFailed |  | Motor not recognized | 0 = No alarm 1 = Alarm |  | bool
00491.8 | [R] | Pump2Alarms4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No alarm 1 = Alarm |  | bool
00491.9 | [R] | Pump2Alarms4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00491.10 | [R] | Pump2Alarms4.DryRunning |  | Dry running | 0 = No alarm 1 = Alarm |  | bool
00491.11 | [R] | Pump2Alarms4.VFDnotReady |  | Variable frequency drive not ready | 0 = No alarm 1 = Alarm |  | bool
00491.12 | [R] | Pump2Alarms4.Other |  | Other | 0 = No alarm 1 = Alarm |  | bool
00491.13 | [R] | Pump2Alarms4.PumpBlocked |  | Pump blocked alarm | 0 = No alarm 1 = Alarm |  | bool
00491.14 | [R] | Pump2Alarms4.SignalFaultPowerSensor |  | Power sensor signal fault alarm | 0 = No alarm 1 = Alarm |  | bool
00492.0 | [R] | Pump2Warnings4.LeakageCurrent |  | Leakage current | 0 = No warning 1 = Warning |  | bool
00492.1 | [R] | Pump2Warnings4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No warning 1 = Warning |  | bool
00492.2 | [R] | Pump2Warnings4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00492.3 | [R] | Pump2Warnings4.Overcurrent |  | Overcurrent | 0 = No warning 1 = Warning |  | bool
00492.4 | [R] | Pump2Warnings4.MotorProtectionActivated |  | Motor protection activated | 0 = No warning 1 = Warning |  | bool
00492.5 | [R] | Pump2Warnings4.ChangeBearings |  | Change bearings | 0 = No warning 1 = Warning |  | bool
00492.6 | [R] | Pump2Warnings4.LubricateBearings |  | Lubricate bearings | 0 = No warning 1 = Warning |  | bool
00492.7 | [R] | Pump2Warnings4.MotorRecognitionFailed |  | Motor not recognized | 0 = No warning 1 = Warning |  | bool
00492.8 | [R] | Pump2Warnings4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No warning 1 = Warning |  | bool
00492.9 | [R] | Pump2Warnings4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00492.10 | [R] | Pump2Warnings4.DryRunning |  | Dry running | 0 = No warning 1 = Warning |  | bool
00492.11 | [R] | Pump2Warnings4.VFDnotReady |  | Variable frequency drive not ready | 0 = No warning 1 = Warning |  | bool
00492.12 | [R] | Pump2Warnings4.Other |  | Other | 0 = No warning 1 = Warning |  | bool
00492.13 | [R] | Pump2Warnings4.PumpBlocked |  | Pump blocked warning | 0 = No alarm 1 = Warning |  | bool
00492.14 | [R] | Pump2Warnings4.SignalFaultPowerSensor |  | Power sensor signal fault warning | 0 = No alarm 1 = Warning |  | bool
00493 | [R] | Pump2AntiBlockingCounter |  | Number of anti blockings in the pump |  |  | unscaled
00494 | [R] | Pump2AISetpointSelect |  | Analog input used as setpoint for pump 2 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00495 | [R] | Pump2SetpointType |  | Setpoint type for pump 2 | 0 = Fixed value 1 = Analog input |  | enum
00496 | [R] | Pump2FeedbackSensorType |  | Feedback sensor type for pump 2 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00497 | [R] | Pump2ControlMode |  | Control mode for pump 2 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00498 | [R] | Pump2ActualSetpoint |  | Actual setpoint for pump 2 |  | 1 | %
00499 | [R] | Pump2FixedFrequency |  | Fixed frequency for pump 2 |  | 0.01 | Hz
PUMP 3 [R]
00501.0 | [R] | Pump3Status.Presence |  | Presence of pump 3 | 0 = No present 1 = Present |  | bool
00501.1 | [R] | Pump3Status.Running |  | Rotation status of pump 3 | 0 = No rotation 1 = Rotation |  | bool
00501.2 | [R] | Pump3Status.MonitoringFault |  | Monitoring status of pump 3 | 0 = No fault 1 = Monitoring fault |  | bool
00501.3 | [R] | Pump3Status.Warning |  | Warning status of pump 3 | 0 = No warning 1 = Warning |  | bool
00501.4 | [R] | Pump3Status.Alarm |  | Alarm status of pump 3 | 0 = No alarm 1 = Alarm |  | bool
00501.5 | [R] | Pump3Status.IO11xPresent |  | IO 11x presence status | 0 = Not present 1 = Present |  | bool
00501.6 | [R] | Pump3Status.IO11xFault |  | IO 11x alarm status | 0 = No alarm 1 = Alarm |  | bool
00501.7 | [R] | Pump3Status.MP204Present |  | MP 204 presence status | 0 = Not present 1 = Present |  | bool
00501.8 | [R] | Pump3Status.MP204Fault |  | MP 204 alarm status | 0 = No alarm 1 = Alarm |  | bool
00501.9 | [R] | Pump3Status.CUEPresent |  | CUE presence status | 0 = Not present 1 = Present |  | bool
00501.10 | [R] | Pump3Status.CUEFault |  | CUE alarm status | 0 = No alarm 1 = Alarm |  | bool
00501.11 | [R] | Pump3Status.PumpDisabled |  | Enabled/Disabled status of pump 3 | 0 = Enabled 1 = Disabled |  | bool
00502 | [R] | Pump3ControlSource |  | Control source of pump 3 | 0 = Auto 1 = Manual by switch 2 = Manual by display 3 = Manual from bus 255 = - |  | enum
00503 | [R] | Pump3ConnectionType |  | Connection type of pump 3 | 0 = CU 36x relay 1 = IO 35x relay 2 = CU 36x+VFD 3 = IO 35x + VFD 255 = - |  | enum
00504 | [R] | Pump3OprTimeHI |  | Operating time of pump 3 |  | 1 | min
00505 | [R] | Pump3OprTimeLO
00506 | [R] | Pump3TimeToServiceHI |  | Time to service for pump 3 |  | 1 | min
00507 | [R] | Pump3TimeToServiceLO
00508 | [R] | Pump3OprTimeYesterday |  | Operating time yesterday, pump 3 |  | 1 | min
00509 | [R] | Pump3OprTimeToday |  | Operating time today, pump 3 |  | 1 | min
00510 | [R] | Pump3LatestOprTime |  | Latest operating time for pump 3 |  | 1 | s
00511 | [R] | Pump3StartCounterHI |  | Start counter for pump 3 |  |  | unscaled
00512 | [R] | Pump3StartCounterLO
00513 | [R] | Pump3StartCounterYesterday |  | Start counter yesterday, pump 3 |  |  | unscaled
00514 | [R] | Pump3StartCounterToday |  | Start counter today, pump 3 |  |  | unscaled
00515 | [R] | Pump3AvgStartsPerHour |  | Average starts per hour for pump 3 |  |  | unscaled
00516 | [R] | Pump3Flow |  | Flow, pump 3 |  | 0.1 | l/s
00517 | [R] | Pump3LatestFlow |  | Latest flow, pump 3 |  | 0.1 | l/s
00518 | [R] | Pump3Current |  | Motor current, pump 3 |  | 0.1 | A
00519 | [R] | Pump3LatestCurrent |  | Latest motor current, pump 3 |  | 0.1 | A
00520 | [R] | Pump3Voltage |  | Motor voltage, pump 3 |  | 0.1 | V
00521 | [R] | Pump3Insulation |  | Motor insulation resistance, pump 3 |  | 10 | kOhm
00522 | [R] | Pump3WaterInOil |  | Water in oil measurement, pump 3 |  | 0.1 | %
00523.0 | [R] | Pump3Alarms1.MotorTemp.alarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No alarm 1 = Alarm |  | bool
00523.1 | [R] | Pump3Alarms1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No alarm 1 = Alarm |  | bool
00523.2 | [R] | Pump3Alarms1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No alarm 1 = Alarm |  | bool
00523.3 | [R] | Pump3Alarms1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No alarm 1 = Alarm |  | bool
00523.4 | [R] | Pump3Alarms1.MotorSupportBearingTemp.High |  | Motor support bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00523.5 | [R] | Pump3Alarms1.MotorMainBearingTemp.High |  | Motor bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00523.6 | [R] | Pump3Alarms1.MotorInsulationRes.Low |  | Motor insulation resistance low | 0 = No alarm 1 = Alarm |  | bool
00523.7 | [R] | Pump3Alarms1.MotorLowVoltage |  | Motor voltage low | 0 = No alarm 1 = Alarm |  | bool
00523.8 | [R] | Pump3Alarms1.MotorHighVoltage |  | Motor voltage high | 0 = No alarm 1 = Alarm |  | bool
00523.9 | [R] | Pump3Alarms1.MotorPhaseSequenceReversal |  | Motor phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00523.10 | [R] | Pump3Alarms1.MotorOverload |  | Motor overload | 0 = No alarm 1 = Alarm |  | bool
00523.11 | [R] | Pump3Alarms1.MotorUnderload |  | Motor underload | 0 = No alarm 1 = Alarm |  | bool
00523.12 | [R] | Pump3Alarms1.MotorProtectorTestTrip |  | Motor protector test trip | 0 = No alarm 1 = Alarm |  | bool
00523.13 | [R] | Pump3Alarms1.MotorMissingPhase |  | Motor missing phase | 0 = No alarm 1 = Alarm |  | bool
00523.14 | [R] | Pump3Alarms1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No alarm 1 = Alarm |  | bool
00523.15 | [R] | Pump3Alarms1.LoadContinuesDespiteMotorRelayisOff |  | Load continues, but motor relay is off | 0 = No alarm 1 = Alarm |  | bool
00524.0 | [R] | Pump3Alarms2.MotorProtectorActivated |  | Motor protector activated | 0 = No alarm 1 = Alarm |  | bool
00524.1 | [R] | Pump3Alarms2.MotorPhaseFailure |  | Motor phase failure | 0 = No alarm 1 = Alarm |  | bool
00524.2 | [R] | Pump3Alarms2.MotorMoistureSwitch |  | Motor moisture | 0 = No alarm 1 = Alarm |  | bool
00524.3 | [R] | Pump3Alarms2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No alarm 1 = Alarm |  | bool
00524.4 | [R] | Pump3Alarms2.WaterInOilLevelTooHigh |  | Water in oil level too high | 0 = No alarm 1 = Alarm |  | bool
00524.5 | [R] | Pump3Alarms2.MotorFaultInMainsSupply |  | Fault in the mains power supply | 0 = No alarm 1 = Alarm |  | bool
00524.6 | [R] | Pump3Alarms2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No alarm 1 = Alarm |  | bool
00524.7 | [R] | Pump3Alarms2.MotorMaxStartsPerHourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00524.8 | [R] | Pump3Alarms2.MotorOperatingTimeServiceLimitExceeded |  | Motor service time exceeded | 0 = No alarm 1 = Alarm |  | bool
00524.9 | [R] | Pump3Alarms2.TooManyPumpAuto-restarts |  | Too many auto restarts of pump | 0 = No alarm 1 = Alarm |  | bool
00524.10 | [R] | Pump3Alarms2.PumpLowFlow |  | Pump low flow | 0 = No alarm 1 = Alarm |  | bool
00524.11 | [R] | Pump3Alarms2.PumpMaxContinuousRun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00524.12 | [R] | Pump3Alarms2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No alarm 1 = Alarm |  | bool
00524.13 | [R] | Pump3Alarms2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No alarm 1 = Alarm |  | bool
00525.0 | [R] | Pump3.Alarms3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No alarm 1 = Alarm |  | bool
00525.1 | [R] | Pump3.Alarms3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No alarm 1 = Alarm |  | bool
00525.2 | [R] | Pump3.Alarms3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No alarm 1 = Alarm |  | bool
00525.3 | [R] | Pump3.Alarms3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No alarm 1 = Alarm |  | bool
00525.4 | [R] | Pump3.Alarms3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No alarm 1 = Alarm |  | bool
00525.5 | [R] | Pump3.Alarms3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No alarm 1 = Alarm |  | bool
00525.6 | [R] | Pump3.Alarms3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00525.7 | [R] | Pump3.Alarms3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00525.8 | [R] | Pump3.Alarms3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No alarm 1 = Alarm |  | bool
00525.9 | [R] | Pump3.Alarms3.SetupConflict |  | Conflict in setup parameters | 0 = No alarm 1 = Alarm |  | bool
00525.10 | [R] | Pump3.Alarms3.GeneralHardwareFault |  | General hardware fault | 0 = No alarm 1 = Alarm |  | bool
00525.11 | [R] | Pump3.Alarms3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No alarm 1 = Alarm |  | bool
00525.12 | [R] | Pump3.Alarms3.InrushFault |  | Inrush fault | 0 = No alarm 1 = Alarm |  | bool
00525.13 | [R] | Pump3.Alarms3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No alarm 1 = Alarm |  | bool
00525.14 | [R] | Pump3.Alarms3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00525.15 | [R] | Pump3.Alarms3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00526.0 | [R] | Pump3Warnings1.MotorTemp.AlarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No warning 1 = Warning |  | bool
00526.1 | [R] | Pump3Warnings1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No warning 1 = Warning |  | bool
00526.2 | [R] | Pump3Warnings1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No warning 1 = Warning |  | bool
00526.3 | [R] | Pump3Warnings1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No warning 1 = Warning |  | bool
00526.4 | [R] | Pump3Warnings1.MotorsupportbearingTemp.High |  | Motor support bearing temperature high | 0 = No warning 1 = Warning |  | bool
00526.5 | [R] | Pump3Warnings1.MotormainbearingTemp.High |  | Motor bearing temperature high | 0 = No warning 1 = Warning |  | bool
00526.6 | [R] | Pump3Warnings1.Motorinsulationres.Low |  | Motor insulation resistance low | 0 = No warning 1 = Warning |  | bool
00526.7 | [R] | Pump3Warnings1.MotorLowVoltage |  | Motor voltage low | 0 = No warning 1 = Warning |  | bool
00526.8 | [R] | Pump3Warnings1.MotorHighVoltage |  | Motor voltage high | 0 = No warning 1 = Warning |  | bool
00526.9 | [R] | Pump3Warnings1.MotorPhasesequencereversal |  | Motor phase sequence reversed | 0 = No warning 1 = Warning |  | bool
00526.10 | [R] | Pump3Warnings1.Motoroverload |  | Motor overload | 0 = No warning 1 = Warning |  | bool
00526.11 | [R] | Pump3Warnings1.Motorunderload |  | Motor underload | 0 = No warning 1 = Warning |  | bool
00526.12 | [R] | Pump3Warnings1.Motorprotectortesttrip |  | Motor protector test trip | 0 = No warning 1 = Warning |  | bool
00526.13 | [R] | Pump3Warnings1.MotormissingPhase |  | Motor missing phase | 0 = No warning 1 = Warning |  | bool
00526.14 | [R] | Pump3Warnings1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No warning 1 = Warning |  | bool
00526.15 | [R] | Pump3Warnings1.LoadContinuesDespiteMotorRelayIsOff |  | Load continues, but motor relay is off | 0 = No warning 1 = Warning |  | bool
00527.0 | [R] | Pump3Warnings2.MotorProtectorActivated |  | Motor protector activated | 0 = No warning 1 = Warning |  | bool
00527.1 | [R] | Pump3Warnings2.MotorPhaseFailure |  | Motor phase failure | 0 = No warning 1 = Warning |  | bool
00527.2 | [R] | Pump3Warnings2.MotorMoistureSwitch |  | Motor moisture | 0 = No warning 1 = Warning |  | bool
00527.3 | [R] | Pump3Warnings2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No warning 1 = Warning |  | bool
00527.4 | [R] | Pump3Warnings2.WaterinoilLevelTooHigh |  | Water in oil level too high | 0 = No warning 1 = Warning |  | bool
00527.5 | [R] | Pump3Warnings2.MotorFaultinmainssupply |  | Fault in the mains power supply | 0 = No warning 1 = Warning |  | bool
00527.6 | [R] | Pump3Warnings2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No warning 1 = Warning |  | bool
00527.7 | [R] | Pump3Warnings2.MotorMaxstartsperhourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No warning 1 = Warning |  | bool
00527.8 | [R] | Pump3Warnings2.MotoroperatingtimeserviceLimitExceeded |  | Motor service time exceeded | 0 = No warning 1 = Warning |  | bool
00527.9 | [R] | Pump3Warnings2.TooManyPumpauto-restarts |  | Too many auto restarts of pump | 0 = No warning 1 = Warning |  | bool
00527.10 | [R] | Pump3Warnings2.PumpLowFlow |  | Pump low flow | 0 = No warning 1 = Warning |  | bool
00527.11 | [R] | Pump3Warnings2.PumpMaxcontinuousrun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No warning 1 = Warning |  | bool
00527.12 | [R] | Pump3Warnings2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No warning 1 = Warning |  | bool
00527.13 | [R] | Pump3Warnings2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No warning 1 = Warning |  | bool
00528.0 | [R] | Pump3.Warnings3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No warning 1 = Warning |  | bool
00528.1 | [R] | Pump3.Warnings3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No warning 1 = Warning |  | bool
00528.2 | [R] | Pump3.Warnings3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No warning 1 = Warning |  | bool
00528.3 | [R] | Pump3.Warnings3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No warning 1 = Warning |  | bool
00528.4 | [R] | Pump3.Warnings3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No warning 1 = Warning |  | bool
00528.5 | [R] | Pump3.Warnings3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No warning 1 = Warning |  | bool
00528.6 | [R] | Pump3.Warnings3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00528.7 | [R] | Pump3.Warnings3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00528.8 | [R] | Pump3.Warnings3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No warning 1 = Warning |  | bool
00528.9 | [R] | Pump3.Warnings3.SetupConflict |  | Conflict in setup parameters | 0 = No warning 1 = Warning |  | bool
00528.10 | [R] | Pump3.Warnings3.GeneralhardwareFault |  | General hardware fault | 0 = No warning 1 = Warning |  | bool
00528.11 | [R] | Pump3.Warnings3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No warning 1 = Warning |  | bool
00528.12 | [R] | Pump3.Warnings3.InrushFault |  | Inrush fault | 0 = No warning 1 = Warning |  | bool
00528.13 | [R] | Pump3.Warnings3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No warning 1 = Warning |  | bool
00528.14 | [R] | Pump3.Warnings3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No warning 1 = Warning |  | bool
00528.15 | [R] | Pump3.Warnings3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No warning 1 = Warning |  | bool
00529 | [R] | Pump3MotorTemperature1 |  | Motor temperature 1, pump 3 |  | 1 | C
00530 | [R] | Pump3MotorTemperature2 |  | Motor temperature 2, pump 3 |  | 1 | C
00531 | [R] | Pump3PowerHI |  | Power consumption, pump 3 |  | 1 | W
00532 | [R] | Pump3PowerLO
00533 | [R] | Pump3EnergyHI |  | Energy consumption, pump 3 |  | 0.1 | kWh
00534 | [R] | Pump3EnergyLO
00535 | [R] | Pump3CosPhi |  | Motor cosine phi, pump 3 |  | 0.01
00536 | [R] | Pump3Frequency |  | Motor applied frequency, pump 3 |  | 0.01 | Hz
00537 | [R] | Pump3VFDmode |  | Mode of variable frequency drive | 0 = Not in control 1 = - 2 = Stopped 3 = Reversed flushing 4 = Start flushing 5 = Normal 6 = Run flushing 255 = - |  | enum
00538 | [R] | Pump3Torque |  | Motor torque, pump 3 |  | 0.1 | Nm
00539 | [R] | Pump3iAsym |  | Line current asymmetry, pump 3 |  | 0.1 | %
00540.0 | [R] | Pump3Sensors.WIO |  | Water-In-Oil sensor | 0 = Not present 1 = Sensor present |  | bool
00540.1 | [R] | Pump3Sensors.Current |  | Motor current sensor | 0 = Not present 1 = Sensor present |  | bool
00541.0 | [R] | Pump3Alarms4.LeakageCurrent |  | Leakage current | 0 = No alarm 1 = Alarm |  | bool
00541.1 | [R] | Pump3Alarms4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No alarm 1 = Alarm |  | bool
00541.2 | [R] | Pump3Alarms4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00541.3 | [R] | Pump3Alarms4.Overcurrent |  | Overcurrent | 0 = No alarm 1 = Alarm |  | bool
00541.4 | [R] | Pump3Alarms4.MotorProtectionActivated |  | Motor protection activated | 0 = No alarm 1 = Alarm |  | bool
00541.5 | [R] | Pump3Alarms4.ChangeBearings |  | Change bearings | 0 = No alarm 1 = Alarm |  | bool
00541.6 | [R] | Pump3Alarms4.LubricateBearings |  | Lubricate bearings | 0 = No alarm 1 = Alarm |  | bool
00541.7 | [R] | Pump3Alarms4.MotorRecognitionFailed |  | Motor not recognized | 0 = No alarm 1 = Alarm |  | bool
00541.8 | [R] | Pump3Alarms4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No alarm 1 = Alarm |  | bool
00541.9 | [R] | Pump3Alarms4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00541.10 | [R] | Pump3Alarms4.DryRunning |  | Dry running | 0 = No alarm 1 = Alarm |  | bool
00541.11 | [R] | Pump3Alarms4.VFDnotReady |  | Variable frequency drive not ready | 0 = No alarm 1 = Alarm |  | bool
00541.12 | [R] | Pump3Alarms4.Other |  | Other | 0 = No alarm 1 = Alarm |  | bool
00541.13 | [R] | Pump3Alarms4.PumpBlocked |  | Pump blocked alarm | 0 = No alarm 1 = Alarm |  | bool
00541.14 | [R] | Pump3Alarms4.SignalFaultPowerSensor |  | Power sensor signal fault alarm | 0 = No alarm 1 = Alarm |  | bool
00542.0 | [R] | Pump3Warnings4.LeakageCurrent |  | Leakage current | 0 = No warning 1 = Warning |  | bool
00542.1 | [R] | Pump3Warnings4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No warning 1 = Warning |  | bool
00542.2 | [R] | Pump3Warnings4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00542.3 | [R] | Pump3Warnings4.Overcurrent |  | Overcurrent | 0 = No warning 1 = Warning |  | bool
00542.4 | [R] | Pump3Warnings4.MotorProtectionActivated |  | Motor protection activated | 0 = No warning 1 = Warning |  | bool
00542.5 | [R] | Pump3Warnings4.ChangeBearings |  | Change bearings | 0 = No warning 1 = Warning |  | bool
00542.6 | [R] | Pump3Warnings4.LubricateBearings |  | Lubricate bearings | 0 = No warning 1 = Warning |  | bool
00542.7 | [R] | Pump3Warnings4.MotorRecognitionFailed |  | Motor not recognized | 0 = No warning 1 = Warning |  | bool
00542.8 | [R] | Pump3Warnings4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No warning 1 = Warning |  | bool
00542.9 | [R] | Pump3Warnings4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00542.10 | [R] | Pump3Warnings4.DryRunning |  | Dry running | 0 = No warning 1 = Warning |  | bool
00542.11 | [R] | Pump3Warnings4.VFDnotReady |  | Variable frequency drive not ready | 0 = No warning 1 = Warning |  | bool
00542.12 | [R] | Pump3Warnings4.Other |  | Other | 0 = No warning 1 = Warning |  | bool
00542.13 | [R] | Pump3Warnings4.PumpBlocked |  | Pump blocked warning | 0 = No alarm 1 = Warning |  | bool
00542.14 | [R] | Pump3Warnings4.SignalFaultPowerSensor |  | Power sensor signal fault warning | 0 = No alarm 1 = Warning |  | bool
00543 | [R] | Pump3AntiBlockingCounter |  | Number of anti blockings in the pump |  |  | unscaled
00544 | [R] | Pump3AISetpointSelect |  | Analog input used as setpoint for pump 3 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00545 | [R] | Pump3SetpointType |  | Setpoint type for pump 3 | 0 = Fixed value 1 = Analog input |  | enum
00546 | [R] | Pump3FeedbackSensorType |  | Feedback sensor type for pump 3 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00547 | [R] | Pump3ControlMode |  | Control mode for pump 3 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00548 | [R] | Pump3ActualSetpoint |  | Actual setpoint for pump 3 |  | 1 | %
00549 | [R] | Pump3FixedFrequency |  | Fixed frequency for pump 3 |  | 0.01 | Hz
PUMP 4 [R]
00551.0 | [R] | Pump4Status.Presence |  | Presence of pump 4 | 0 = No present 1 = Present |  | bool
00551.1 | [R] | Pump4Status.Running |  | Rotation status of pump 4 | 0 = No rotation 1 = Rotation |  | bool
00551.2 | [R] | Pump4Status.MonitoringFault |  | Monitoring status of pump 4 | 0 = No fault 1 = Monitoring fault |  | bool
00551.3 | [R] | Pump4Status.Warning |  | Warning status of pump 4 | 0 = No warning 1 = Warning |  | bool
00551.4 | [R] | Pump4Status.Alarm |  | Alarm status of pump 4 | 0 = No alarm 1 = Alarm |  | bool
00551.5 | [R] | Pump4Status.IO11xPresent |  | IO 11x presence status | 0 = Not present 1 = Present |  | bool
00551.6 | [R] | Pump4Status.IO11xFault |  | IO 11x alarm status | 0 = No alarm 1 = Alarm |  | bool
00551.7 | [R] | Pump4Status.MP204Present |  | MP 204 presence status | 0 = Not present 1 = Present |  | bool
00551.8 | [R] | Pump4Status.MP204Fault |  | MP 204 alarm status | 0 = No alarm 1 = Alarm |  | bool
00551.9 | [R] | Pump4Status.CUEPresent |  | CUE presence status | 0 = Not present 1 = Present |  | bool
00551.10 | [R] | Pump4Status.CUEFault |  | CUE alarm status | 0 = No alarm 1 = Alarm |  | bool
00551.11 | [R] | Pump4Status.PumpDisabled |  | Enabled/Disabled status of pump 4 | 0 = Enabled 1 = Disabled |  | bool
00552 | [R] | Pump4ControlSource |  | Control source of pump 4 | 0 = Auto 1 = Manual by switch 2 = Manual by display 3 = Manual from bus 255 = - |  | enum
00553 | [R] | Pump4ConnectionType |  | Connection type of pump 4 | 0 = CU 36x relay 1 = IO 35x relay 2 = CU 36x+VFD 3 = IO 35x + VFD 255 = - |  | enum
00554 | [R] | Pump4OprTimeHI |  | Operating time of pump 4 |  | 1 | min
00555 | [R] | Pump4OprTimeLO
00556 | [R] | Pump4TimeToServiceHI |  | Time to service for pump 4 |  | 1 | min
00557 | [R] | Pump4TimeToServiceLO
00558 | [R] | Pump4OprTimeYesterday |  | Operating time yesterday, pump 4 |  | 1 | min
00559 | [R] | Pump4OprTimeToday |  | Operating time today, pump 4 |  | 1 | min
00560 | [R] | Pump4LatestOprTime |  | Latest operating time for pump 4 |  | 1 | s
00561 | [R] | Pump4StartCounterHI |  | Start counter for pump 4 |  |  | unscaled
00562 | [R] | Pump4StartCounterLO
00563 | [R] | Pump4StartCounterYesterday |  | Start counter yesterday, pump 4 |  |  | unscaled
00564 | [R] | Pump4StartCounterToday |  | Start counter today, pump 4 |  |  | unscaled
00565 | [R] | Pump4AvgStartsPerHour |  | Average starts per hour for pump 4 |  |  | unscaled
00566 | [R] | Pump4Flow |  | Flow, pump 4 |  | 0.1 | l/s
00567 | [R] | Pump4LatestFlow |  | Latest flow, pump 4 |  | 0.1 | l/s
00568 | [R] | Pump4Current |  | Motor current, pump 4 |  | 0.1 | A
00569 | [R] | Pump4LatestCurrent |  | Latest motor current, pump 4 |  | 0.1 | A
00570 | [R] | Pump4Voltage |  | Motor voltage, pump 4 |  | 0.1 | V
00571 | [R] | Pump4Insulation |  | Motor insulation resistance, pump 4 |  | 10 | kOhm
00572 | [R] | Pump4WaterInOil |  | Water in oil measurement, pump 4 |  | 0.1 | %
00573.0 | [R] | Pump4Alarms1.MotorTemp.alarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No alarm 1 = Alarm |  | bool
00573.1 | [R] | Pump4Alarms1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No alarm 1 = Alarm |  | bool
00573.2 | [R] | Pump4Alarms1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No alarm 1 = Alarm |  | bool
00573.3 | [R] | Pump4Alarms1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No alarm 1 = Alarm |  | bool
00573.4 | [R] | Pump4Alarms1.MotorSupportBearingTemp.High |  | Motor support bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00573.5 | [R] | Pump4Alarms1.MotorMainBearingTemp.High |  | Motor bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00573.6 | [R] | Pump4Alarms1.MotorInsulationRes.Low |  | Motor insulation resistance low | 0 = No alarm 1 = Alarm |  | bool
00573.7 | [R] | Pump4Alarms1.MotorLowVoltage |  | Motor voltage low | 0 = No alarm 1 = Alarm |  | bool
00573.8 | [R] | Pump4Alarms1.MotorHighVoltage |  | Motor voltage high | 0 = No alarm 1 = Alarm |  | bool
00573.9 | [R] | Pump4Alarms1.MotorPhaseSequenceReversal |  | Motor phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00573.10 | [R] | Pump4Alarms1.MotorOverload |  | Motor overload | 0 = No alarm 1 = Alarm |  | bool
00573.11 | [R] | Pump4Alarms1.MotorUnderload |  | Motor underload | 0 = No alarm 1 = Alarm |  | bool
00573.12 | [R] | Pump4Alarms1.MotorProtectorTestTrip |  | Motor protector test trip | 0 = No alarm 1 = Alarm |  | bool
00573.13 | [R] | Pump4Alarms1.MotorMissingPhase |  | Motor missing phase | 0 = No alarm 1 = Alarm |  | bool
00573.14 | [R] | Pump4Alarms1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No alarm 1 = Alarm |  | bool
00573.15 | [R] | Pump4Alarms1.LoadContinuesDespiteMotorRelayisOff |  | Load continues, but motor relay is off | 0 = No alarm 1 = Alarm |  | bool
00574.0 | [R] | Pump4Alarms2.MotorProtectorActivated |  | Motor protector activated | 0 = No alarm 1 = Alarm |  | bool
00574.1 | [R] | Pump4Alarms2.MotorPhaseFailure |  | Motor phase failure | 0 = No alarm 1 = Alarm |  | bool
00574.2 | [R] | Pump4Alarms2.MotorMoistureSwitch |  | Motor moisture | 0 = No alarm 1 = Alarm |  | bool
00574.3 | [R] | Pump4Alarms2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No alarm 1 = Alarm |  | bool
00574.4 | [R] | Pump4Alarms2.WaterInOilLevelTooHigh |  | Water in oil level too high | 0 = No alarm 1 = Alarm |  | bool
00574.5 | [R] | Pump4Alarms2.MotorFaultInMainsSupply |  | Fault in the mains power supply | 0 = No alarm 1 = Alarm |  | bool
00574.6 | [R] | Pump4Alarms2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No alarm 1 = Alarm |  | bool
00574.7 | [R] | Pump4Alarms2.MotorMaxStartsPerHourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00574.8 | [R] | Pump4Alarms2.MotorOperatingTimeServiceLimitExceeded |  | Motor service time exceeded | 0 = No alarm 1 = Alarm |  | bool
00574.9 | [R] | Pump4Alarms2.TooManyPumpAuto-restarts |  | Too many auto restarts of pump | 0 = No alarm 1 = Alarm |  | bool
00574.10 | [R] | Pump4Alarms2.PumpLowFlow |  | Pump low flow | 0 = No alarm 1 = Alarm |  | bool
00574.11 | [R] | Pump4Alarms2.PumpMaxContinuousRun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00574.12 | [R] | Pump4Alarms2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No alarm 1 = Alarm |  | bool
00574.13 | [R] | Pump4Alarms2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No alarm 1 = Alarm |  | bool
00575.0 | [R] | Pump4.Alarms3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No alarm 1 = Alarm |  | bool
00575.1 | [R] | Pump4.Alarms3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No alarm 1 = Alarm |  | bool
00575.2 | [R] | Pump4.Alarms3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No alarm 1 = Alarm |  | bool
00575.3 | [R] | Pump4.Alarms3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No alarm 1 = Alarm |  | bool
00575.4 | [R] | Pump4.Alarms3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No alarm 1 = Alarm |  | bool
00575.5 | [R] | Pump4.Alarms3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No alarm 1 = Alarm |  | bool
00575.6 | [R] | Pump4.Alarms3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00575.7 | [R] | Pump4.Alarms3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00575.8 | [R] | Pump4.Alarms3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No alarm 1 = Alarm |  | bool
00575.9 | [R] | Pump4.Alarms3.SetupConflict |  | Conflict in setup parameters | 0 = No alarm 1 = Alarm |  | bool
00575.10 | [R] | Pump4.Alarms3.GeneralHardwareFault |  | General hardware fault | 0 = No alarm 1 = Alarm |  | bool
00575.11 | [R] | Pump4.Alarms3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No alarm 1 = Alarm |  | bool
00575.12 | [R] | Pump4.Alarms3.InrushFault |  | Inrush fault | 0 = No alarm 1 = Alarm |  | bool
00575.13 | [R] | Pump4.Alarms3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No alarm 1 = Alarm |  | bool
00575.14 | [R] | Pump4.Alarms3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00575.15 | [R] | Pump4.Alarms3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00576.0 | [R] | Pump4Warnings1.MotorTemp.AlarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No warning 1 = Warning |  | bool
00576.1 | [R] | Pump4Warnings1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No warning 1 = Warning |  | bool
00576.2 | [R] | Pump4Warnings1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No warning 1 = Warning |  | bool
00576.3 | [R] | Pump4Warnings1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No warning 1 = Warning |  | bool
00576.4 | [R] | Pump4Warnings1.MotorsupportbearingTemp.High |  | Motor support bearing temperature high | 0 = No warning 1 = Warning |  | bool
00576.5 | [R] | Pump4Warnings1.MotormainbearingTemp.High |  | Motor bearing temperature high | 0 = No warning 1 = Warning |  | bool
00576.6 | [R] | Pump4Warnings1.Motorinsulationres.Low |  | Motor insulation resistance low | 0 = No warning 1 = Warning |  | bool
00576.7 | [R] | Pump4Warnings1.MotorLowVoltage |  | Motor voltage low | 0 = No warning 1 = Warning |  | bool
00576.8 | [R] | Pump4Warnings1.MotorHighVoltage |  | Motor voltage high | 0 = No warning 1 = Warning |  | bool
00576.9 | [R] | Pump4Warnings1.MotorPhasesequencereversal |  | Motor phase sequence reversed | 0 = No warning 1 = Warning |  | bool
00576.10 | [R] | Pump4Warnings1.Motoroverload |  | Motor overload | 0 = No warning 1 = Warning |  | bool
00576.11 | [R] | Pump4Warnings1.Motorunderload |  | Motor underload | 0 = No warning 1 = Warning |  | bool
00576.12 | [R] | Pump4Warnings1.Motorprotectortesttrip |  | Motor protector test trip | 0 = No warning 1 = Warning |  | bool
00576.13 | [R] | Pump4Warnings1.MotormissingPhase |  | Motor missing phase | 0 = No warning 1 = Warning |  | bool
00576.14 | [R] | Pump4Warnings1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No warning 1 = Warning |  | bool
00576.15 | [R] | Pump4Warnings1.LoadContinuesDespiteMotorRelayIsOff |  | Load continues, but motor relay is off | 0 = No warning 1 = Warning |  | bool
00577.0 | [R] | Pump4Warnings2.MotorProtectorActivated |  | Motor protector activated | 0 = No warning 1 = Warning |  | bool
00577.1 | [R] | Pump4Warnings2.MotorPhaseFailure |  | Motor phase failure | 0 = No warning 1 = Warning |  | bool
00577.2 | [R] | Pump4Warnings2.MotorMoistureSwitch |  | Motor moisture | 0 = No warning 1 = Warning |  | bool
00577.3 | [R] | Pump4Warnings2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No warning 1 = Warning |  | bool
00577.4 | [R] | Pump4Warnings2.WaterinoilLevelTooHigh |  | Water in oil level too high | 0 = No warning 1 = Warning |  | bool
00577.5 | [R] | Pump4Warnings2.MotorFaultinmainssupply |  | Fault in the mains power supply | 0 = No warning 1 = Warning |  | bool
00577.6 | [R] | Pump4Warnings2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No warning 1 = Warning |  | bool
00577.7 | [R] | Pump4Warnings2.MotorMaxstartsperhourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No warning 1 = Warning |  | bool
00577.8 | [R] | Pump4Warnings2.MotoroperatingtimeserviceLimitExceeded |  | Motor service time exceeded | 0 = No warning 1 = Warning |  | bool
00577.9 | [R] | Pump4Warnings2.TooManyPumpauto-restarts |  | Too many auto restarts of pump | 0 = No warning 1 = Warning |  | bool
00577.10 | [R] | Pump4Warnings2.PumpLowFlow |  | Pump low flow | 0 = No warning 1 = Warning |  | bool
00577.11 | [R] | Pump4Warnings2.PumpMaxcontinuousrun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No warning 1 = Warning |  | bool
00577.12 | [R] | Pump4Warnings2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No warning 1 = Warning |  | bool
00577.13 | [R] | Pump4Warnings2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No warning 1 = Warning |  | bool
00578.0 | [R] | Pump4.Warnings3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No warning 1 = Warning |  | bool
00578.1 | [R] | Pump4.Warnings3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No warning 1 = Warning |  | bool
00578.2 | [R] | Pump4.Warnings3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No warning 1 = Warning |  | bool
00578.3 | [R] | Pump4.Warnings3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No warning 1 = Warning |  | bool
00578.4 | [R] | Pump4.Warnings3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No warning 1 = Warning |  | bool
00578.5 | [R] | Pump4.Warnings3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No warning 1 = Warning |  | bool
00578.6 | [R] | Pump4.Warnings3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00578.7 | [R] | Pump4.Warnings3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00578.8 | [R] | Pump4.Warnings3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No warning 1 = Warning |  | bool
00578.9 | [R] | Pump4.Warnings3.SetupConflict |  | Conflict in setup parameters | 0 = No warning 1 = Warning |  | bool
00578.10 | [R] | Pump4.Warnings3.GeneralhardwareFault |  | General hardware fault | 0 = No warning 1 = Warning |  | bool
00578.11 | [R] | Pump4.Warnings3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No warning 1 = Warning |  | bool
00578.12 | [R] | Pump4.Warnings3.InrushFault |  | Inrush fault | 0 = No warning 1 = Warning |  | bool
00578.13 | [R] | Pump4.Warnings3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No warning 1 = Warning |  | bool
00578.14 | [R] | Pump4.Warnings3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No warning 1 = Warning |  | bool
00578.15 | [R] | Pump4.Warnings3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No warning 1 = Warning |  | bool
00579 | [R] | Pump4MotorTemperature1 |  | Motor temperature 1, pump 4 |  | 1 | C
00580 | [R] | Pump4MotorTemperature2 |  | Motor temperature 2, pump 4 |  | 1 | C
00581 | [R] | Pump4PowerHI |  | Power consumption, pump 4 |  | 1 | W
00582 | [R] | Pump4PowerLO
00583 | [R] | Pump4EnergyHI |  | Energy consumption, pump 4 |  | 0.1 | kWh
00584 | [R] | Pump4EnergyLO
00585 | [R] | Pump4CosPhi |  | Motor cosine phi, pump 4 |  | 0.01
00586 | [R] | Pump4Frequency |  | Motor applied frequency, pump 4 |  | 0.01 | Hz
00587 | [R] | Pump4VFDmode |  | Mode of variable frequency drive | 0 = Not in control 1 = - 2 = Stopped 3 = Reversed flushing 4 = Start flushing 5 = Normal 6 = Run flushing 255 = - |  | enum
00588 | [R] | Pump4Torque |  | Motor torque, pump 4 |  | 0.1 | Nm
00589 | [R] | Pump4iAsym |  | Line current asymmetry, pump 4 |  | 0.1 | %
00590.0 | [R] | Pump4Sensors.WIO |  | Water-In-Oil sensor | 0 = Not present 1 = Sensor present |  | bool
00590.1 | [R] | Pump4Sensors.Current |  | Motor current sensor | 0 = Not present 1 = Sensor present |  | bool
00591.0 | [R] | Pump4Alarms4.LeakageCurrent |  | Leakage current | 0 = No alarm 1 = Alarm |  | bool
00591.1 | [R] | Pump4Alarms4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No alarm 1 = Alarm |  | bool
00591.2 | [R] | Pump4Alarms4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00591.3 | [R] | Pump4Alarms4.Overcurrent |  | Overcurrent | 0 = No alarm 1 = Alarm |  | bool
00591.4 | [R] | Pump4Alarms4.MotorProtectionActivated |  | Motor protection activated | 0 = No alarm 1 = Alarm |  | bool
00591.5 | [R] | Pump4Alarms4.ChangeBearings |  | Change bearings | 0 = No alarm 1 = Alarm |  | bool
00591.6 | [R] | Pump4Alarms4.LubricateBearings |  | Lubricate bearings | 0 = No alarm 1 = Alarm |  | bool
00591.7 | [R] | Pump4Alarms4.MotorRecognitionFailed |  | Motor not recognized | 0 = No alarm 1 = Alarm |  | bool
00591.8 | [R] | Pump4Alarms4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No alarm 1 = Alarm |  | bool
00591.9 | [R] | Pump4Alarms4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00591.10 | [R] | Pump4Alarms4.DryRunning |  | Dry running | 0 = No alarm 1 = Alarm |  | bool
00591.11 | [R] | Pump4Alarms4.VFDnotReady |  | Variable frequency drive not ready | 0 = No alarm 1 = Alarm |  | bool
00591.12 | [R] | Pump4Alarms4.Other |  | Other | 0 = No alarm 1 = Alarm |  | bool
00591.13 | [R] | Pump4Alarms4.PumpBlocked |  | Pump blocked alarm | 0 = No alarm 1 = Alarm |  | bool
00591.14 | [R] | Pump4Alarms4.SignalFaultPowerSensor |  | Power sensor signal fault alarm | 0 = No alarm 1 = Alarm |  | bool
00592.0 | [R] | Pump4Warnings4.LeakageCurrent |  | Leakage current | 0 = No warning 1 = Warning |  | bool
00592.1 | [R] | Pump4Warnings4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No warning 1 = Warning |  | bool
00592.2 | [R] | Pump4Warnings4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00592.3 | [R] | Pump4Warnings4.Overcurrent |  | Overcurrent | 0 = No warning 1 = Warning |  | bool
00592.4 | [R] | Pump4Warnings4.MotorProtectionActivated |  | Motor protection activated | 0 = No warning 1 = Warning |  | bool
00592.5 | [R] | Pump4Warnings4.ChangeBearings |  | Change bearings | 0 = No warning 1 = Warning |  | bool
00592.6 | [R] | Pump4Warnings4.LubricateBearings |  | Lubricate bearings | 0 = No warning 1 = Warning |  | bool
00592.7 | [R] | Pump4Warnings4.MotorRecognitionFailed |  | Motor not recognized | 0 = No warning 1 = Warning |  | bool
00592.8 | [R] | Pump4Warnings4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No warning 1 = Warning |  | bool
00592.9 | [R] | Pump4Warnings4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00592.10 | [R] | Pump4Warnings4.DryRunning |  | Dry running | 0 = No warning 1 = Warning |  | bool
00592.11 | [R] | Pump4Warnings4.VFDnotReady |  | Variable frequency drive not ready | 0 = No warning 1 = Warning |  | bool
00592.12 | [R] | Pump4Warnings4.Other |  | Other | 0 = No warning 1 = Warning |  | bool
00592.13 | [R] | Pump4Warnings4.PumpBlocked |  | Pump blocked warning | 0 = No alarm 1 = Warning |  | bool
00592.14 | [R] | Pump4Warnings4.SignalFaultPowerSensor |  | Power sensor signal fault warning | 0 = No alarm 1 = Warning |  | bool
00593 | [R] | Pump4AntiBlockingCounter |  | Number of anti blockings in the pump |  |  | unscaled
00594 | [R] | Pump4AISetpointSelect |  | Analog input used as setpoint for pump 4 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00595 | [R] | Pump4SetpointType |  | Setpoint type for pump 4 | 0 = Fixed value 1 = Analog input |  | enum
00596 | [R] | Pump4FeedbackSensorType |  | Feedback sensor type for pump 4 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00597 | [R] | Pump4ControlMode |  | Control mode for pump 4 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00598 | [R] | Pump4ActualSetpoint |  | Actual setpoint for pump 4 |  | 1 | %
00599 | [R] | Pump4FixedFrequency |  | Fixed frequency for pump 4 |  | 0.01 | Hz
PUMP 5 [R]
00601.0 | [R] | Pump5Status.Presence |  | Presence of pump 5 | 0 = No present 1 = Present |  | bool
00601.1 | [R] | Pump5Status.Running |  | Rotation status of pump 5 | 0 = No rotation 1 = Rotation |  | bool
00601.2 | [R] | Pump5Status.MonitoringFault |  | Monitoring status of pump 5 | 0 = No fault 1 = Monitoring fault |  | bool
00601.3 | [R] | Pump5Status.Warning |  | Warning status of pump 5 | 0 = No warning 1 = Warning |  | bool
00601.4 | [R] | Pump5Status.Alarm |  | Alarm status of pump 5 | 0 = No alarm 1 = Alarm |  | bool
00601.5 | [R] | Pump5Status.IO11xPresent |  | IO 11x presence status | 0 = Not present 1 = Present |  | bool
00601.6 | [R] | Pump5Status.IO11xFault |  | IO 11x alarm status | 0 = No alarm 1 = Alarm |  | bool
00601.7 | [R] | Pump5Status.MP204Present |  | MP 204 presence status | 0 = Not present 1 = Present |  | bool
00601.8 | [R] | Pump5Status.MP204Fault |  | MP 204 alarm status | 0 = No alarm 1 = Alarm |  | bool
00601.9 | [R] | Pump5Status.CUEPresent |  | CUE presence status | 0 = Not present 1 = Present |  | bool
00601.10 | [R] | Pump5Status.CUEFault |  | CUE alarm status | 0 = No alarm 1 = Alarm |  | bool
00601.11 | [R] | Pump5Status.PumpDisabled |  | Enabled/Disabled status of pump 5 | 0 = Enabled 1 = Disabled |  | bool
00602 | [R] | Pump5ControlSource |  | Control source of pump 5 | 0 = Auto 1 = Manual by switch 2 = Manual by display 3 = Manual from bus 255 = - |  | enum
00603 | [R] | Pump5ConnectionType |  | Connection type of pump 5 | 0 = CU 36x relay 1 = IO 35x relay 2 = CU 36x+VFD 3 = IO 35x + VFD 255 = - |  | enum
00604 | [R] | Pump5OprTimeHI |  | Operating time of pump 5 |  | 1 | min
00605 | [R] | Pump5OprTimeLO
00606 | [R] | Pump5TimeToServiceHI |  | Time to service for pump 5 |  | 1 | min
00607 | [R] | Pump5TimeToServiceLO
00608 | [R] | Pump5OprTimeYesterday |  | Operating time yesterday, pump 5 |  | 1 | min
00609 | [R] | Pump5OprTimeToday |  | Operating time today, pump 5 |  | 1 | min
00610 | [R] | Pump5LatestOprTime |  | Latest operating time for pump 5 |  | 1 | s
00611 | [R] | Pump5StartCounterHI |  | Start counter for pump 5 |  |  | unscaled
00612 | [R] | Pump5StartCounterLO
00613 | [R] | Pump5StartCounterYesterday |  | Start counter yesterday, pump 5 |  |  | unscaled
00614 | [R] | Pump5StartCounterToday |  | Start counter today, pump 5 |  |  | unscaled
00615 | [R] | Pump5AvgStartsPerHour |  | Average starts per hour for pump 5 |  |  | unscaled
00616 | [R] | Pump5Flow |  | Flow, pump 5 |  | 0.1 | l/s
00617 | [R] | Pump5LatestFlow |  | Latest flow, pump 5 |  | 0.1 | l/s
00618 | [R] | Pump5Current |  | Motor current, pump 5 |  | 0.1 | A
00619 | [R] | Pump5LatestCurrent |  | Latest motor current, pump 5 |  | 0.1 | A
00620 | [R] | Pump5Voltage |  | Motor voltage, pump 5 |  | 0.1 | V
00621 | [R] | Pump5Insulation |  | Motor insulation resistance, pump 5 |  | 10 | kOhm
00622 | [R] | Pump5WaterInOil |  | Water in oil measurement, pump 5 |  | 0.1 | %
00623.0 | [R] | Pump5Alarms1.MotorTemp.alarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No alarm 1 = Alarm |  | bool
00623.1 | [R] | Pump5Alarms1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No alarm 1 = Alarm |  | bool
00623.2 | [R] | Pump5Alarms1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No alarm 1 = Alarm |  | bool
00623.3 | [R] | Pump5Alarms1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No alarm 1 = Alarm |  | bool
00623.4 | [R] | Pump5Alarms1.MotorSupportBearingTemp.High |  | Motor support bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00623.5 | [R] | Pump5Alarms1.MotorMainBearingTemp.High |  | Motor bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00623.6 | [R] | Pump5Alarms1.MotorInsulationRes.Low |  | Motor insulation resistance low | 0 = No alarm 1 = Alarm |  | bool
00623.7 | [R] | Pump5Alarms1.MotorLowVoltage |  | Motor voltage low | 0 = No alarm 1 = Alarm |  | bool
00623.8 | [R] | Pump5Alarms1.MotorHighVoltage |  | Motor voltage high | 0 = No alarm 1 = Alarm |  | bool
00623.9 | [R] | Pump5Alarms1.MotorPhaseSequenceReversal |  | Motor phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00623.10 | [R] | Pump5Alarms1.MotorOverload |  | Motor overload | 0 = No alarm 1 = Alarm |  | bool
00623.11 | [R] | Pump5Alarms1.MotorUnderload |  | Motor underload | 0 = No alarm 1 = Alarm |  | bool
00623.12 | [R] | Pump5Alarms1.MotorProtectorTestTrip |  | Motor protector test trip | 0 = No alarm 1 = Alarm |  | bool
00623.13 | [R] | Pump5Alarms1.MotorMissingPhase |  | Motor missing phase | 0 = No alarm 1 = Alarm |  | bool
00623.14 | [R] | Pump5Alarms1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No alarm 1 = Alarm |  | bool
00623.15 | [R] | Pump5Alarms1.LoadContinuesDespiteMotorRelayisOff |  | Load continues, but motor relay is off | 0 = No alarm 1 = Alarm |  | bool
00624.0 | [R] | Pump5Alarms2.MotorProtectorActivated |  | Motor protector activated | 0 = No alarm 1 = Alarm |  | bool
00624.1 | [R] | Pump5Alarms2.MotorPhaseFailure |  | Motor phase failure | 0 = No alarm 1 = Alarm |  | bool
00624.2 | [R] | Pump5Alarms2.MotorMoistureSwitch |  | Motor moisture | 0 = No alarm 1 = Alarm |  | bool
00624.3 | [R] | Pump5Alarms2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No alarm 1 = Alarm |  | bool
00624.4 | [R] | Pump5Alarms2.WaterInOilLevelTooHigh |  | Water in oil level too high | 0 = No alarm 1 = Alarm |  | bool
00624.5 | [R] | Pump5Alarms2.MotorFaultInMainsSupply |  | Fault in the mains power supply | 0 = No alarm 1 = Alarm |  | bool
00624.6 | [R] | Pump5Alarms2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No alarm 1 = Alarm |  | bool
00624.7 | [R] | Pump5Alarms2.MotorMaxStartsPerHourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00624.8 | [R] | Pump5Alarms2.MotorOperatingTimeServiceLimitExceeded |  | Motor service time exceeded | 0 = No alarm 1 = Alarm |  | bool
00624.9 | [R] | Pump5Alarms2.TooManyPumpAuto-restarts |  | Too many auto restarts of pump | 0 = No alarm 1 = Alarm |  | bool
00624.10 | [R] | Pump5Alarms2.PumpLowFlow |  | Pump low flow | 0 = No alarm 1 = Alarm |  | bool
00624.11 | [R] | Pump5Alarms2.PumpMaxContinuousRun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00624.12 | [R] | Pump5Alarms2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No alarm 1 = Alarm |  | bool
00624.13 | [R] | Pump5Alarms2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No alarm 1 = Alarm |  | bool
00625.0 | [R] | Pump5.Alarms3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No alarm 1 = Alarm |  | bool
00625.1 | [R] | Pump5.Alarms3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No alarm 1 = Alarm |  | bool
00625.2 | [R] | Pump5.Alarms3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No alarm 1 = Alarm |  | bool
00625.3 | [R] | Pump5.Alarms3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No alarm 1 = Alarm |  | bool
00625.4 | [R] | Pump5.Alarms3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No alarm 1 = Alarm |  | bool
00625.5 | [R] | Pump5.Alarms3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No alarm 1 = Alarm |  | bool
00625.6 | [R] | Pump5.Alarms3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00625.7 | [R] | Pump5.Alarms3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00625.8 | [R] | Pump5.Alarms3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No alarm 1 = Alarm |  | bool
00625.9 | [R] | Pump5.Alarms3.SetupConflict |  | Conflict in setup parameters | 0 = No alarm 1 = Alarm |  | bool
00625.10 | [R] | Pump5.Alarms3.GeneralHardwareFault |  | General hardware fault | 0 = No alarm 1 = Alarm |  | bool
00625.11 | [R] | Pump5.Alarms3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No alarm 1 = Alarm |  | bool
00625.12 | [R] | Pump5.Alarms3.InrushFault |  | Inrush fault | 0 = No alarm 1 = Alarm |  | bool
00625.13 | [R] | Pump5.Alarms3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No alarm 1 = Alarm |  | bool
00625.14 | [R] | Pump5.Alarms3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00625.15 | [R] | Pump5.Alarms3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00626.0 | [R] | Pump5Warnings1.MotorTemp.AlarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No warning 1 = Warning |  | bool
00626.1 | [R] | Pump5Warnings1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No warning 1 = Warning |  | bool
00626.2 | [R] | Pump5Warnings1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No warning 1 = Warning |  | bool
00626.3 | [R] | Pump5Warnings1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No warning 1 = Warning |  | bool
00626.4 | [R] | Pump5Warnings1.MotorsupportbearingTemp.High |  | Motor support bearing temperature high | 0 = No warning 1 = Warning |  | bool
00626.5 | [R] | Pump5Warnings1.MotormainbearingTemp.High |  | Motor bearing temperature high | 0 = No warning 1 = Warning |  | bool
00626.6 | [R] | Pump5Warnings1.Motorinsulationres.Low |  | Motor insulation resistance low | 0 = No warning 1 = Warning |  | bool
00626.7 | [R] | Pump5Warnings1.MotorLowVoltage |  | Motor voltage low | 0 = No warning 1 = Warning |  | bool
00626.8 | [R] | Pump5Warnings1.MotorHighVoltage |  | Motor voltage high | 0 = No warning 1 = Warning |  | bool
00626.9 | [R] | Pump5Warnings1.MotorPhasesequencereversal |  | Motor phase sequence reversed | 0 = No warning 1 = Warning |  | bool
00626.10 | [R] | Pump5Warnings1.Motoroverload |  | Motor overload | 0 = No warning 1 = Warning |  | bool
00626.11 | [R] | Pump5Warnings1.Motorunderload |  | Motor underload | 0 = No warning 1 = Warning |  | bool
00626.12 | [R] | Pump5Warnings1.Motorprotectortesttrip |  | Motor protector test trip | 0 = No warning 1 = Warning |  | bool
00626.13 | [R] | Pump5Warnings1.MotormissingPhase |  | Motor missing phase | 0 = No warning 1 = Warning |  | bool
00626.14 | [R] | Pump5Warnings1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No warning 1 = Warning |  | bool
00626.15 | [R] | Pump5Warnings1.LoadContinuesDespiteMotorRelayIsOff |  | Load continues, but motor relay is off | 0 = No warning 1 = Warning |  | bool
00627.0 | [R] | Pump5Warnings2.MotorProtectorActivated |  | Motor protector activated | 0 = No warning 1 = Warning |  | bool
00627.1 | [R] | Pump5Warnings2.MotorPhaseFailure |  | Motor phase failure | 0 = No warning 1 = Warning |  | bool
00627.2 | [R] | Pump5Warnings2.MotorMoistureSwitch |  | Motor moisture | 0 = No warning 1 = Warning |  | bool
00627.3 | [R] | Pump5Warnings2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No warning 1 = Warning |  | bool
00627.4 | [R] | Pump5Warnings2.WaterinoilLevelTooHigh |  | Water in oil level too high | 0 = No warning 1 = Warning |  | bool
00627.5 | [R] | Pump5Warnings2.MotorFaultinmainssupply |  | Fault in the mains power supply | 0 = No warning 1 = Warning |  | bool
00627.6 | [R] | Pump5Warnings2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No warning 1 = Warning |  | bool
00627.7 | [R] | Pump5Warnings2.MotorMaxstartsperhourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No warning 1 = Warning |  | bool
00627.8 | [R] | Pump5Warnings2.MotoroperatingtimeserviceLimitExceeded |  | Motor service time exceeded | 0 = No warning 1 = Warning |  | bool
00627.9 | [R] | Pump5Warnings2.TooManyPumpauto-restarts |  | Too many auto restarts of pump | 0 = No warning 1 = Warning |  | bool
00627.10 | [R] | Pump5Warnings2.PumpLowFlow |  | Pump low flow | 0 = No warning 1 = Warning |  | bool
00627.11 | [R] | Pump5Warnings2.PumpMaxcontinuousrun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No warning 1 = Warning |  | bool
00627.12 | [R] | Pump5Warnings2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No warning 1 = Warning |  | bool
00627.13 | [R] | Pump5Warnings2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No warning 1 = Warning |  | bool
00628.0 | [R] | Pump5.Warnings3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No warning 1 = Warning |  | bool
00628.1 | [R] | Pump5.Warnings3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No warning 1 = Warning |  | bool
00628.2 | [R] | Pump5.Warnings3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No warning 1 = Warning |  | bool
00628.3 | [R] | Pump5.Warnings3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No warning 1 = Warning |  | bool
00628.4 | [R] | Pump5.Warnings3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No warning 1 = Warning |  | bool
00628.5 | [R] | Pump5.Warnings3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No warning 1 = Warning |  | bool
00628.6 | [R] | Pump5.Warnings3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00628.7 | [R] | Pump5.Warnings3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00628.8 | [R] | Pump5.Warnings3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No warning 1 = Warning |  | bool
00628.9 | [R] | Pump5.Warnings3.SetupConflict |  | Conflict in setup parameters | 0 = No warning 1 = Warning |  | bool
00628.10 | [R] | Pump5.Warnings3.GeneralhardwareFault |  | General hardware fault | 0 = No warning 1 = Warning |  | bool
00628.11 | [R] | Pump5.Warnings3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No warning 1 = Warning |  | bool
00628.12 | [R] | Pump5.Warnings3.InrushFault |  | Inrush fault | 0 = No warning 1 = Warning |  | bool
00628.13 | [R] | Pump5.Warnings3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No warning 1 = Warning |  | bool
00628.14 | [R] | Pump5.Warnings3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No warning 1 = Warning |  | bool
00628.15 | [R] | Pump5.Warnings3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No warning 1 = Warning |  | bool
00629 | [R] | Pump5MotorTemperature1 |  | Motor temperature 1, pump 5 |  | 1 | C
00630 | [R] | Pump5MotorTemperature2 |  | Motor temperature 2, pump 5 |  | 1 | C
00631 | [R] | Pump5PowerHI |  | Power consumption, pump 5 |  | 1 | W
00632 | [R] | Pump5PowerLO
00633 | [R] | Pump5EnergyHI |  | Energy consumption, pump 5 |  | 0.1 | kWh
00634 | [R] | Pump5EnergyLO
00635 | [R] | Pump5CosPhi |  | Motor cosine phi, pump 5 |  | 0.01
00636 | [R] | Pump5Frequency |  | Motor applied frequency, pump 5 |  | 0.01 | Hz
00637 | [R] | Pump5VFDmode |  | Mode of variable frequency drive | 0 = Not in control 1 = - 2 = Stopped 3 = Reversed flushing 4 = Start flushing 5 = Normal 6 = Run flushing 255 = - |  | enum
00638 | [R] | Pump5Torque |  | Motor torque, pump 5 |  | 0.1 | Nm
00639 | [R] | Pump5iAsym |  | Line current asymmetry, pump 5 |  | 0.1 | %
00640.0 | [R] | Pump5Sensors.WIO |  | Water-In-Oil sensor | 0 = Not present 1 = Sensor present |  | bool
00640.1 | [R] | Pump5Sensors.Current |  | Motor current sensor | 0 = Not present 1 = Sensor present |  | bool
00641.0 | [R] | Pump5Alarms4.LeakageCurrent |  | Leakage current | 0 = No alarm 1 = Alarm |  | bool
00641.1 | [R] | Pump5Alarms4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No alarm 1 = Alarm |  | bool
00641.2 | [R] | Pump5Alarms4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00641.3 | [R] | Pump5Alarms4.Overcurrent |  | Overcurrent | 0 = No alarm 1 = Alarm |  | bool
00641.4 | [R] | Pump5Alarms4.MotorProtectionActivated |  | Motor protection activated | 0 = No alarm 1 = Alarm |  | bool
00641.5 | [R] | Pump5Alarms4.ChangeBearings |  | Change bearings | 0 = No alarm 1 = Alarm |  | bool
00641.6 | [R] | Pump5Alarms4.LubricateBearings |  | Lubricate bearings | 0 = No alarm 1 = Alarm |  | bool
00641.7 | [R] | Pump5Alarms4.MotorRecognitionFailed |  | Motor not recognized | 0 = No alarm 1 = Alarm |  | bool
00641.8 | [R] | Pump5Alarms4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No alarm 1 = Alarm |  | bool
00641.9 | [R] | Pump5Alarms4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00641.10 | [R] | Pump5Alarms4.DryRunning |  | Dry running | 0 = No alarm 1 = Alarm |  | bool
00641.11 | [R] | Pump5Alarms4.VFDnotReady |  | Variable frequency drive not ready | 0 = No alarm 1 = Alarm |  | bool
00641.12 | [R] | Pump5Alarms4.Other |  | Other | 0 = No alarm 1 = Alarm |  | bool
00641.13 | [R] | Pump5Alarms4.PumpBlocked |  | Pump blocked alarm | 0 = No alarm 1 = Alarm |  | bool
00641.14 | [R] | Pump5Alarms4.SignalFaultPowerSensor |  | Power sensor signal fault alarm | 0 = No alarm 1 = Alarm |  | bool
00642.0 | [R] | Pump5Warnings4.LeakageCurrent |  | Leakage current | 0 = No warning 1 = Warning |  | bool
00642.1 | [R] | Pump5Warnings4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No warning 1 = Warning |  | bool
00642.2 | [R] | Pump5Warnings4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00642.3 | [R] | Pump5Warnings4.Overcurrent |  | Overcurrent | 0 = No warning 1 = Warning |  | bool
00642.4 | [R] | Pump5Warnings4.MotorProtectionActivated |  | Motor protection activated | 0 = No warning 1 = Warning |  | bool
00642.5 | [R] | Pump5Warnings4.ChangeBearings |  | Change bearings | 0 = No warning 1 = Warning |  | bool
00642.6 | [R] | Pump5Warnings4.LubricateBearings |  | Lubricate bearings | 0 = No warning 1 = Warning |  | bool
00642.7 | [R] | Pump5Warnings4.MotorRecognitionFailed |  | Motor not recognized | 0 = No warning 1 = Warning |  | bool
00642.8 | [R] | Pump5Warnings4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No warning 1 = Warning |  | bool
00642.9 | [R] | Pump5Warnings4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00642.10 | [R] | Pump5Warnings4.DryRunning |  | Dry running | 0 = No warning 1 = Warning |  | bool
00642.11 | [R] | Pump5Warnings4.VFDnotReady |  | Variable frequency drive not ready | 0 = No warning 1 = Warning |  | bool
00642.12 | [R] | Pump5Warnings4.Other |  | Other | 0 = No warning 1 = Warning |  | bool
00642.13 | [R] | Pump5Warnings4.PumpBlocked |  | Pump blocked warning | 0 = No alarm 1 = Warning |  | bool
00642.14 | [R] | Pump5Warnings4.SignalFaultPowerSensor |  | Power sensor signal fault warning | 0 = No alarm 1 = Warning |  | bool
00643 | [R] | Pump5AntiBlockingCounter |  | Number of anti blockings in the pump |  |  | unscaled
00644 | [R] | Pump5AISetpointSelect |  | Analog input used as setpoint for pump 5 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00645 | [R] | Pump5SetpointType |  | Setpoint type for pump 5 | 0 = Fixed value 1 = Analog input |  | enum
00646 | [R] | Pump5FeedbackSensorType |  | Feedback sensor type for pump 5 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00647 | [R] | Pump5ControlMode |  | Control mode for pump 5 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00648 | [R] | Pump5ActualSetpoint |  | Actual setpoint for pump 5 |  | 1 | %
00649 | [R] | Pump5FixedFrequency |  | Fixed frequency for pump 5 |  | 0.01 | Hz
PUMP 6 [R]
00651.0 | [R] | Pump6Status.Presence |  | Presence of pump 6 | 0 = No present 1 = Present |  | bool
00651.1 | [R] | Pump6Status.Running |  | Rotation status of pump 6 | 0 = No rotation 1 = Rotation |  | bool
00651.2 | [R] | Pump6Status.MonitoringFault |  | Monitoring status of pump 6 | 0 = No fault 1 = Monitoring fault |  | bool
00651.3 | [R] | Pump6Status.Warning |  | Warning status of pump 6 | 0 = No warning 1 = Warning |  | bool
00651.4 | [R] | Pump6Status.Alarm |  | Alarm status of pump 6 | 0 = No alarm 1 = Alarm |  | bool
00651.5 | [R] | Pump6Status.IO11xPresent |  | IO 11x presence status | 0 = Not present 1 = Present |  | bool
00651.6 | [R] | Pump6Status.IO11xFault |  | IO 11x alarm status | 0 = No alarm 1 = Alarm |  | bool
00651.7 | [R] | Pump6Status.MP204Present |  | MP 204 presence status | 0 = Not present 1 = Present |  | bool
00651.8 | [R] | Pump6Status.MP204Fault |  | MP 204 alarm status | 0 = No alarm 1 = Alarm |  | bool
00651.9 | [R] | Pump6Status.CUEPresent |  | CUE presence status | 0 = Not present 1 = Present |  | bool
00651.10 | [R] | Pump6Status.CUEFault |  | CUE alarm status | 0 = No alarm 1 = Alarm |  | bool
00651.11 | [R] | Pump6Status.PumpDisabled |  | Enabled/Disabled status of pump 6 | 0 = Enabled 1 = Disabled |  | bool
00652 | [R] | Pump6ControlSource |  | Control source of pump 6 | 0 = Auto 1 = Manual by switch 2 = Manual by display 3 = Manual from bus 255 = - |  | enum
00653 | [R] | Pump6ConnectionType |  | Connection type of pump 6 | 0 = CU 36x relay 1 = IO 35x relay 2 = CU 36x+VFD 3 = IO 35x + VFD 255 = - |  | enum
00654 | [R] | Pump6OprTimeHI |  | Operating time of pump 6 |  | 1 | min
00655 | [R] | Pump6OprTimeLO
00656 | [R] | Pump6TimeToServiceHI |  | Time to service for pump 6 |  | 1 | min
00657 | [R] | Pump6TimeToServiceLO
00658 | [R] | Pump6OprTimeYesterday |  | Operating time yesterday, pump 6 |  | 1 | min
00659 | [R] | Pump6OprTimeToday |  | Operating time today, pump 6 |  | 1 | min
00660 | [R] | Pump6LatestOprTime |  | Latest operating time for pump 6 |  | 1 | s
00661 | [R] | Pump6StartCounterHI |  | Start counter for pump 6 |  |  | unscaled
00662 | [R] | Pump6StartCounterLO
00663 | [R] | Pump6StartCounterYesterday |  | Start counter yesterday, pump 6 |  |  | unscaled
00664 | [R] | Pump6StartCounterToday |  | Start counter today, pump 6 |  |  | unscaled
00665 | [R] | Pump6AvgStartsPerHour |  | Average starts per hour for pump 6 |  |  | unscaled
00666 | [R] | Pump6Flow |  | Flow, pump 6 |  | 0.1 | l/s
00667 | [R] | Pump6LatestFlow |  | Latest flow, pump 6 |  | 0.1 | l/s
00668 | [R] | Pump6Current |  | Motor current, pump 6 |  | 0.1 | A
00669 | [R] | Pump6LatestCurrent |  | Latest motor current, pump 6 |  | 0.1 | A
00670 | [R] | Pump6Voltage |  | Motor voltage, pump 6 |  | 0.1 | V
00671 | [R] | Pump6Insulation |  | Motor insulation resistance, pump 6 |  | 10 | kOhm
00672 | [R] | Pump6WaterInOil |  | Water in oil measurement, pump 6 |  | 0.1 | %
00673.0 | [R] | Pump6Alarms1.MotorTemp.alarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No alarm 1 = Alarm |  | bool
00673.1 | [R] | Pump6Alarms1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No alarm 1 = Alarm |  | bool
00673.2 | [R] | Pump6Alarms1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No alarm 1 = Alarm |  | bool
00673.3 | [R] | Pump6Alarms1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No alarm 1 = Alarm |  | bool
00673.4 | [R] | Pump6Alarms1.MotorSupportBearingTemp.High |  | Motor support bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00673.5 | [R] | Pump6Alarms1.MotorMainBearingTemp.High |  | Motor bearing temperature high | 0 = No alarm 1 = Alarm |  | bool
00673.6 | [R] | Pump6Alarms1.MotorInsulationRes.Low |  | Motor insulation resistance low | 0 = No alarm 1 = Alarm |  | bool
00673.7 | [R] | Pump6Alarms1.MotorLowVoltage |  | Motor voltage low | 0 = No alarm 1 = Alarm |  | bool
00673.8 | [R] | Pump6Alarms1.MotorHighVoltage |  | Motor voltage high | 0 = No alarm 1 = Alarm |  | bool
00673.9 | [R] | Pump6Alarms1.MotorPhaseSequenceReversal |  | Motor phase sequence reversed | 0 = No alarm 1 = Alarm |  | bool
00673.10 | [R] | Pump6Alarms1.MotorOverload |  | Motor overload | 0 = No alarm 1 = Alarm |  | bool
00673.11 | [R] | Pump6Alarms1.MotorUnderload |  | Motor underload | 0 = No alarm 1 = Alarm |  | bool
00673.12 | [R] | Pump6Alarms1.MotorProtectorTestTrip |  | Motor protector test trip | 0 = No alarm 1 = Alarm |  | bool
00673.13 | [R] | Pump6Alarms1.MotorMissingPhase |  | Motor missing phase | 0 = No alarm 1 = Alarm |  | bool
00673.14 | [R] | Pump6Alarms1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No alarm 1 = Alarm |  | bool
00673.15 | [R] | Pump6Alarms1.LoadContinuesDespiteMotorRelayisOff |  | Load continues, but motor relay is off | 0 = No alarm 1 = Alarm |  | bool
00674.0 | [R] | Pump6Alarms2.MotorProtectorActivated |  | Motor protector activated | 0 = No alarm 1 = Alarm |  | bool
00674.1 | [R] | Pump6Alarms2.MotorPhaseFailure |  | Motor phase failure | 0 = No alarm 1 = Alarm |  | bool
00674.2 | [R] | Pump6Alarms2.MotorMoistureSwitch |  | Motor moisture | 0 = No alarm 1 = Alarm |  | bool
00674.3 | [R] | Pump6Alarms2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No alarm 1 = Alarm |  | bool
00674.4 | [R] | Pump6Alarms2.WaterInOilLevelTooHigh |  | Water in oil level too high | 0 = No alarm 1 = Alarm |  | bool
00674.5 | [R] | Pump6Alarms2.MotorFaultInMainsSupply |  | Fault in the mains power supply | 0 = No alarm 1 = Alarm |  | bool
00674.6 | [R] | Pump6Alarms2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No alarm 1 = Alarm |  | bool
00674.7 | [R] | Pump6Alarms2.MotorMaxStartsPerHourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00674.8 | [R] | Pump6Alarms2.MotorOperatingTimeServiceLimitExceeded |  | Motor service time exceeded | 0 = No alarm 1 = Alarm |  | bool
00674.9 | [R] | Pump6Alarms2.TooManyPumpAuto-restarts |  | Too many auto restarts of pump | 0 = No alarm 1 = Alarm |  | bool
00674.10 | [R] | Pump6Alarms2.PumpLowFlow |  | Pump low flow | 0 = No alarm 1 = Alarm |  | bool
00674.11 | [R] | Pump6Alarms2.PumpMaxContinuousRun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No alarm 1 = Alarm |  | bool
00674.12 | [R] | Pump6Alarms2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No alarm 1 = Alarm |  | bool
00674.13 | [R] | Pump6Alarms2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No alarm 1 = Alarm |  | bool
00675.0 | [R] | Pump6.Alarms3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No alarm 1 = Alarm |  | bool
00675.1 | [R] | Pump6.Alarms3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No alarm 1 = Alarm |  | bool
00675.2 | [R] | Pump6.Alarms3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No alarm 1 = Alarm |  | bool
00675.3 | [R] | Pump6.Alarms3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No alarm 1 = Alarm |  | bool
00675.4 | [R] | Pump6.Alarms3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No alarm 1 = Alarm |  | bool
00675.5 | [R] | Pump6.Alarms3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No alarm 1 = Alarm |  | bool
00675.6 | [R] | Pump6.Alarms3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00675.7 | [R] | Pump6.Alarms3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No alarm 1 = Alarm |  | bool
00675.8 | [R] | Pump6.Alarms3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No alarm 1 = Alarm |  | bool
00675.9 | [R] | Pump6.Alarms3.SetupConflict |  | Conflict in setup parameters | 0 = No alarm 1 = Alarm |  | bool
00675.10 | [R] | Pump6.Alarms3.GeneralHardwareFault |  | General hardware fault | 0 = No alarm 1 = Alarm |  | bool
00675.11 | [R] | Pump6.Alarms3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No alarm 1 = Alarm |  | bool
00675.12 | [R] | Pump6.Alarms3.InrushFault |  | Inrush fault | 0 = No alarm 1 = Alarm |  | bool
00675.13 | [R] | Pump6.Alarms3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No alarm 1 = Alarm |  | bool
00675.14 | [R] | Pump6.Alarms3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00675.15 | [R] | Pump6.Alarms3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No alarm 1 = Alarm |  | bool
00676.0 | [R] | Pump6Warnings1.MotorTemp.AlarmPTC1 |  | Motor temperature PTC1 alarm | 0 = No warning 1 = Warning |  | bool
00676.1 | [R] | Pump6Warnings1.MotorTemp.alarmPTC2 |  | Motor Temperature PTC2 alarm | 0 = No warning 1 = Warning |  | bool
00676.2 | [R] | Pump6Warnings1.MotorStatorTemp.High(T1) |  | Motor Stator Temperature (T1) | 0 = No warning 1 = Warning |  | bool
00676.3 | [R] | Pump6Warnings1.MotorStatorTemp.High(T2) |  | Motor Stator Temperature (T2) | 0 = No warning 1 = Warning |  | bool
00676.4 | [R] | Pump6Warnings1.MotorsupportbearingTemp.High |  | Motor support bearing temperature high | 0 = No warning 1 = Warning |  | bool
00676.5 | [R] | Pump6Warnings1.MotormainbearingTemp.High |  | Motor bearing temperature high | 0 = No warning 1 = Warning |  | bool
00676.6 | [R] | Pump6Warnings1.Motorinsulationres.Low |  | Motor insulation resistance low | 0 = No warning 1 = Warning |  | bool
00676.7 | [R] | Pump6Warnings1.MotorLowVoltage |  | Motor voltage low | 0 = No warning 1 = Warning |  | bool
00676.8 | [R] | Pump6Warnings1.MotorHighVoltage |  | Motor voltage high | 0 = No warning 1 = Warning |  | bool
00676.9 | [R] | Pump6Warnings1.MotorPhasesequencereversal |  | Motor phase sequence reversed | 0 = No warning 1 = Warning |  | bool
00676.10 | [R] | Pump6Warnings1.Motoroverload |  | Motor overload | 0 = No warning 1 = Warning |  | bool
00676.11 | [R] | Pump6Warnings1.Motorunderload |  | Motor underload | 0 = No warning 1 = Warning |  | bool
00676.12 | [R] | Pump6Warnings1.Motorprotectortesttrip |  | Motor protector test trip | 0 = No warning 1 = Warning |  | bool
00676.13 | [R] | Pump6Warnings1.MotormissingPhase |  | Motor missing phase | 0 = No warning 1 = Warning |  | bool
00676.14 | [R] | Pump6Warnings1.MotorCurrentAsymmetry |  | Motor current asymmetry | 0 = No warning 1 = Warning |  | bool
00676.15 | [R] | Pump6Warnings1.LoadContinuesDespiteMotorRelayIsOff |  | Load continues, but motor relay is off | 0 = No warning 1 = Warning |  | bool
00677.0 | [R] | Pump6Warnings2.MotorProtectorActivated |  | Motor protector activated | 0 = No warning 1 = Warning |  | bool
00677.1 | [R] | Pump6Warnings2.MotorPhaseFailure |  | Motor phase failure | 0 = No warning 1 = Warning |  | bool
00677.2 | [R] | Pump6Warnings2.MotorMoistureSwitch |  | Motor moisture | 0 = No warning 1 = Warning |  | bool
00677.3 | [R] | Pump6Warnings2.Motor/PumpVibrationHigh |  | Pump vibration too high | 0 = No warning 1 = Warning |  | bool
00677.4 | [R] | Pump6Warnings2.WaterinoilLevelTooHigh |  | Water in oil level too high | 0 = No warning 1 = Warning |  | bool
00677.5 | [R] | Pump6Warnings2.MotorFaultinmainssupply |  | Fault in the mains power supply | 0 = No warning 1 = Warning |  | bool
00677.6 | [R] | Pump6Warnings2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No warning 1 = Warning |  | bool
00677.7 | [R] | Pump6Warnings2.MotorMaxstartsperhourLimitExceeded |  | Motor max starts per hour limit exceeded | 0 = No warning 1 = Warning |  | bool
00677.8 | [R] | Pump6Warnings2.MotoroperatingtimeserviceLimitExceeded |  | Motor service time exceeded | 0 = No warning 1 = Warning |  | bool
00677.9 | [R] | Pump6Warnings2.TooManyPumpauto-restarts |  | Too many auto restarts of pump | 0 = No warning 1 = Warning |  | bool
00677.10 | [R] | Pump6Warnings2.PumpLowFlow |  | Pump low flow | 0 = No warning 1 = Warning |  | bool
00677.11 | [R] | Pump6Warnings2.PumpMaxcontinuousrun-timeLimitExceeded |  | Pump max continuous runtime limit exceeded | 0 = No warning 1 = Warning |  | bool
00677.12 | [R] | Pump6Warnings2.MotorCosPhiTooHigh |  | Motor cosine phi too high | 0 = No warning 1 = Warning |  | bool
00677.13 | [R] | Pump6Warnings2.MotorCosPhiTooLow |  | Motor cosine phi too low | 0 = No warning 1 = Warning |  | bool
00678.0 | [R] | Pump6.Warnings3.Pumpmalfunctionduetoaux.componentFault |  | Fault in auxilary component | 0 = No warning 1 = Warning |  | bool
00678.1 | [R] | Pump6.Warnings3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump communication | 0 = No warning 1 = Warning |  | bool
00678.2 | [R] | Pump6.Warnings3.On/Off/AutoSwitchFault |  | Fault in manual switch | 0 = No warning 1 = Warning |  | bool
00678.3 | [R] | Pump6.Warnings3.PT100SensorSignalFault |  | PT 100 sensor fault | 0 = No warning 1 = Warning |  | bool
00678.4 | [R] | Pump6.Warnings3.PTCSensorSignalFault |  | PTC sensor fault | 0 = No warning 1 = Warning |  | bool
00678.5 | [R] | Pump6.Warnings3.Waterinoil(WIO)SensorSignalFault |  | Water-in-oil sensor fault | 0 = No warning 1 = Warning |  | bool
00678.6 | [R] | Pump6.Warnings3.MotorsupportbearingTemp.SensorSignalFault |  | Motor support bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00678.7 | [R] | Pump6.Warnings3.MotormainbearingTemp.SensorSignalFault |  | Motor main bearing temperature sensor fault | 0 = No warning 1 = Warning |  | bool
00678.8 | [R] | Pump6.Warnings3.Pump(Powerline)comm.Fault |  | Pump communication fault | 0 = No warning 1 = Warning |  | bool
00678.9 | [R] | Pump6.Warnings3.SetupConflict |  | Conflict in setup parameters | 0 = No warning 1 = Warning |  | bool
00678.10 | [R] | Pump6.Warnings3.GeneralhardwareFault |  | General hardware fault | 0 = No warning 1 = Warning |  | bool
00678.11 | [R] | Pump6.Warnings3.MotorCurrentSensorSignalFault |  | Motor current sensor signal | 0 = No warning 1 = Warning |  | bool
00678.12 | [R] | Pump6.Warnings3.InrushFault |  | Inrush fault | 0 = No warning 1 = Warning |  | bool
00678.13 | [R] | Pump6.Warnings3.SignalFaultSensor2 |  | Signal fault sensor 2 | 0 = No warning 1 = Warning |  | bool
00678.14 | [R] | Pump6.Warnings3.MotorBearingTempHigh, DE |  | Motor bearing drive end temperature | 0 = No warning 1 = Warning |  | bool
00678.15 | [R] | Pump6.Warnings3.MotorBearingTempHigh, N-DE |  | Motor bearing non-drive end temperature | 0 = No warning 1 = Warning |  | bool
00679 | [R] | Pump6MotorTemperature1 |  | Motor temperature 1, pump 6 |  | 1 | C
00680 | [R] | Pump6MotorTemperature2 |  | Motor temperature 2, pump 6 |  | 1 | C
00681 | [R] | Pump6PowerHI |  | Power consumption, pump 6 |  | 1 | W
00682 | [R] | Pump6PowerLO
00683 | [R] | Pump6EnergyHI |  | Energy consumption, pump 6 |  | 0.1 | kWh
00684 | [R] | Pump6EnergyLO
00685 | [R] | Pump6CosPhi |  | Motor cosine phi, pump 6 |  | 0.01
00686 | [R] | Pump6Frequency |  | Motor applied frequency, pump 6 |  | 0.01 | Hz
00687 | [R] | Pump6VFDmode |  | Mode of variable frequency drive | 0 = Not in control 1 = - 2 = Stopped 3 = Reversed flushing 4 = Start flushing 5 = Normal 6 = Run flushing 255 = - |  | enum
00688 | [R] | Pump6Torque |  | Motor torque, pump 6 |  | 0.1 | Nm
00689 | [R] | Pump6iAsym |  | Line current asymmetry, pump 6 |  | 0.1 | %
00690.0 | [R] | Pump6Sensors.WIO |  | Water-In-Oil sensor | 0 = Not present 1 = Sensor present |  | bool
00690.1 | [R] | Pump6Sensors.Current |  | Motor current sensor | 0 = Not present 1 = Sensor present |  | bool
00691.0 | [R] | Pump6Alarms4.LeakageCurrent |  | Leakage current | 0 = No alarm 1 = Alarm |  | bool
00691.1 | [R] | Pump6Alarms4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No alarm 1 = Alarm |  | bool
00691.2 | [R] | Pump6Alarms4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00691.3 | [R] | Pump6Alarms4.Overcurrent |  | Overcurrent | 0 = No alarm 1 = Alarm |  | bool
00691.4 | [R] | Pump6Alarms4.MotorProtectionActivated |  | Motor protection activated | 0 = No alarm 1 = Alarm |  | bool
00691.5 | [R] | Pump6Alarms4.ChangeBearings |  | Change bearings | 0 = No alarm 1 = Alarm |  | bool
00691.6 | [R] | Pump6Alarms4.LubricateBearings |  | Lubricate bearings | 0 = No alarm 1 = Alarm |  | bool
00691.7 | [R] | Pump6Alarms4.MotorRecognitionFailed |  | Motor not recognized | 0 = No alarm 1 = Alarm |  | bool
00691.8 | [R] | Pump6Alarms4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No alarm 1 = Alarm |  | bool
00691.9 | [R] | Pump6Alarms4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No alarm 1 = Alarm |  | bool
00691.10 | [R] | Pump6Alarms4.DryRunning |  | Dry running | 0 = No alarm 1 = Alarm |  | bool
00691.11 | [R] | Pump6Alarms4.VFDnotReady |  | Variable frequency drive not ready | 0 = No alarm 1 = Alarm |  | bool
00691.12 | [R] | Pump6Alarms4.Other |  | Other | 0 = No alarm 1 = Alarm |  | bool
00691.13 | [R] | Pump6Alarms4.PumpBlocked |  | Pump blocked alarm | 0 = No alarm 1 = Alarm |  | bool
00691.14 | [R] | Pump6Alarms4.SignalFaultPowerSensor |  | Power sensor signal fault alarm | 0 = No alarm 1 = Alarm |  | bool
00692.0 | [R] | Pump6Warnings4.LeakageCurrent |  | Leakage current | 0 = No warning 1 = Warning |  | bool
00692.1 | [R] | Pump6Warnings4.SignalFaultTemp3Sensor |  | Temperature sensor 3 fault | 0 = No warning 1 = Warning |  | bool
00692.2 | [R] | Pump6Warnings4.SignalFaultSensor1 |  | Sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00692.3 | [R] | Pump6Warnings4.Overcurrent |  | Overcurrent | 0 = No warning 1 = Warning |  | bool
00692.4 | [R] | Pump6Warnings4.MotorProtectionActivated |  | Motor protection activated | 0 = No warning 1 = Warning |  | bool
00692.5 | [R] | Pump6Warnings4.ChangeBearings |  | Change bearings | 0 = No warning 1 = Warning |  | bool
00692.6 | [R] | Pump6Warnings4.LubricateBearings |  | Lubricate bearings | 0 = No warning 1 = Warning |  | bool
00692.7 | [R] | Pump6Warnings4.MotorRecognitionFailed |  | Motor not recognized | 0 = No warning 1 = Warning |  | bool
00692.8 | [R] | Pump6Warnings4.CommFaultTwinHead |  | Communication fault - twin head | 0 = No warning 1 = Warning |  | bool
00692.9 | [R] | Pump6Warnings4.SignalFaultTemp1Sensor |  | Temperature sensor 1 fault | 0 = No warning 1 = Warning |  | bool
00692.10 | [R] | Pump6Warnings4.DryRunning |  | Dry running | 0 = No warning 1 = Warning |  | bool
00692.11 | [R] | Pump6Warnings4.VFDnotReady |  | Variable frequency drive not ready | 0 = No warning 1 = Warning |  | bool
00692.12 | [R] | Pump6Warnings4.Other |  | Other | 0 = No warning 1 = Warning |  | bool
00692.13 | [R] | Pump6Warnings4.PumpBlocked |  | Pump blocked warning | 0 = No alarm 1 = Warning |  | bool
00692.14 | [R] | Pump6Warnings4.SignalFaultPowerSensor |  | Power sensor signal fault warning | 0 = No alarm 1 = Warning |  | bool
00693 | [R] | Pump6AntiBlockingCounter |  | Number of anti blockings in the pump |  |  | unscaled
00694 | [R] | Pump6AISetpointSelect |  | Analog input used as setpoint for pump 6 | 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00695 | [R] | Pump6SetpointType |  | Setpoint type for pump 6 | 0 = Fixed value 1 = Analog input |  | enum
00696 | [R] | Pump6FeedbackSensorType |  | Feedback sensor type for pump 6 | 4 = Flow rate 5 = Level, pressure 6 = Level, Ultrasound 13 = User defined Sensor 1 14 = User defined sensor 2 15 = User defined sensor 3 |  | enum
00697 | [R] | Pump6ControlMode |  | Control mode for pump 6 | 0 = Fixed Frequency 1 = Linear Control 2 = Minimum Control 3 = PID control |  | enum
00698 | [R] | Pump6ActualSetpoint |  | Actual setpoint for pump 6 |  | 1 | %
00699 | [R] | Pump6FixedFrequency |  | Fixed frequency for pump 6 |  | 0.01 | Hz
SIMULATION [R/W]
00701 | [W] | Simulation.EventCode | Event code to simulate | Event code to simulate |  |  | enum
00702 | [W] | Simulation.EventSource | Device type generating event | Device type that generates the event |  |  | enum
00703 | [W] | Simulation.EventDeviceNo | Number of the device | Event device number |  |  | enum
00704 | [W] | Simulation.EventActionType | 0=Warn, 1=Alarm, 2=Disable | Event-Action type | 0 = Warning 1 = Alarm 2 = Disabled |  | enum
00705 | [W] | Simulation.Activate |  | Activate event simulation | 0 = Deactivate 1 = Activate |  | bool
00706 | [R] | Simulation.Status |  | Status of event simulation | 0 = Disabled 1 = Enabled |  | bool
USER REGISTERS [R/W]
00751 | [R/W] | UserLabel1 | Saved in EEPROM |  |  |  | unscaled
00752 | [R/W] | UserLabel2 | Saved in EEPROM |  |  |  | unscaled
00753 | [R/W] | UserLabel3 | Saved in EEPROM |  |  |  | unscaled
00754-00799 | [R/W] | UserLabel4...UserLabel49 | Saved in EEPROM |  |  |  | unscaled
00800 | [R/W] | UserLabel50 | Saved in EEPROM |  |  |  | unscaled
DISPLAY NAME STRING [R]
00801 | [R] | NameRegister1 | Modbus reads in object |  |  |  | UTF8-char
00802 | [R] | NameRegister2 | Modbus reads in object |  |  |  | UTF8-char
00803-00920 | [R] | NameRegister3-NameRegister120 | Modbus reads in object |  |  |  | UTF8-char
HOUR LOG [R]
02001-02072 | [R] | PitOverflowTimeHourLog1…72 |  |  |  |  | 1 min
02073-02144 | [R] | PitOverflowCntHourLog1…72 |  |  |  |  | unscaled
02145-02216 | [R] | PitOverflowVolumeHourLog1…72 |  |  |  |  | 0.1 m3
02217-02288 | [R] | PitSpecificEnergyHourLog1…72 |  |  |  |  | 1 Wh/m3
02289-02360 | [R] | PitVolumeHourLog1…72 |  |  |  |  | 0.1 m3
02361-02432 | [R] | PitEnergyHourLog1…72 |  |  |  |  | 0.1 kWh
02433 | [R] | Pit2PumpsOprTimeHourLog1…72 |  |  |  |  | 1 min
02505 | [R] | Pit3PumpsOprTimeHourLog1…72 |  |  |  |  | 1 min
02577 | [R] | Pit4PumpsOprTimeHourLog1…72 |  |  |  |  | 1 min
02649 | [R] | Pit5PumpsOprTimeHourLog1…72 |  |  |  |  | 1 min
02721 | [R] | Pit6PumpsOprTimeHourLog1…72 |  |  |  |  | 1 min
02793 | [R] | Pump1OprTimeHourLog1…72 |  |  |  |  | 1 min
02865 | [R] | Pump1StartCntHourLog1…72 |  |  |  |  | unscaled
02937 | [R] | Pump1AvgFlowHourLog1…72 |  |  |  |  | 0.1 liter/s
03009 | [R] | Pump1AvgCurrentHourLog…72 |  |  |  |  | 0.1 A
03081 | [R] | Pump2OprTimeHourLog1…72 |  |  |  |  | 1 min
03153 | [R] | Pump2StartCntHourLog1…72 |  |  |  |  | unscaled
03225 | [R] | Pump2AvgFlowHourLog1…72 |  |  |  |  | 0.1 liter/s
03297 | [R] | Pump2AvgCurrentHourLog…72 |  |  |  |  | 0.1 A
03369 | [R] | Pump3OprTimeHourLog1…72 |  |  |  |  | 1 min
03441 | [R] | Pump3StartCntHourLog1…72 |  |  |  |  | unscaled
03513 | [R] | Pump3AvgFlowHourLog1…72 |  |  |  |  | 0.1 liter/s
03585 | [R] | Pump3AvgCurrentHourLog…72 |  |  |  |  | 0.1 A
03657 | [R] | Pump4OprTimeHourLog1…72 |  |  |  |  | 1 min
03729 | [R] | Pump4StartCntHourLog1…72 |  |  |  |  | unscaled
03801 | [R] | Pump4AvgFlowHourLog1…72 |  |  |  |  | 0.1 liter/s
03873 | [R] | Pump4AvgCurrentHourLog…72 |  |  |  |  | 0.1 A
03945 | [R] | Pump5OprTimeHourLog1…72 |  |  |  |  | 1 min
04017 | [R] | Pump5StartCntHourLog1…72 |  |  |  |  | unscaled
04089 | [R] | Pump5AvgFlowHourLog1…72 |  |  |  |  | 0.1 liter/s
04161 | [R] | Pump5AvgCurrentHourLog…72 |  |  |  |  | 0.1 A
04233 | [R] | Pump6OprTimeHourLog1…72 |  |  |  |  | 1 min
04305 | [R] | Pump6StartCntHourLog1…72 |  |  |  |  | unscaled
04377 | [R] | Pump6AvgFlowHourLog1…72 |  |  |  |  | 0.1 liter/s
04449 | [R] | Pump6AvgCurrentHourLog…72 |  |  |  |  | 0.1 A
EVENT LOG [R]
06001 | [R] | NoOfEventsInLog |  |  |  |  | unscaled
06002 | [R] | EventIDLog1 |  |  |  |  | unscaled
06003 | [R] | EventCodeLog1 |  |  |  |  | enum
06004 | [R] | EventSourceLog1 |  |  |  |  | enum
06005 | [R] | EventDeviceNo |  |  |  |  | unscaled
06006 | [R] | EventTypeAndConditionLog1 |  |  |  |  | enum
06007 | [R] | EventTimeStampLog1HI |  |  |  |  | 1 s
06008 | [R] | EventTimeStampLog1LO
06009 | [R] | EventIDLog2 |  |  |  |  | unscaled
06010 | [R] | EventCodeLog2 |  |  |  |  | enum
06011 | [R] | EventSourceLog2 |  |  |  |  | enum
06012 | [R] | EventDeviceNo |  |  |  |  | unscaled
06013 | [R] | EventTypeAndConditionLog2 |  |  |  |  | enum
06014 | [R] | EventTimeStampLog2HI |  |  |  |  | 1 s
06015 | [R] | EventTimeStampLog2LO
Continue list for event logs 3 - 49
06345 | [R] | EventIDLog50 |  |  |  |  | unscaled
06346 | [R] | EventCodeLog50 |  |  |  |  | enum
06347 | [R] | EventSourceLog50 |  |  |  |  | enum
06348 | [R] | EventDeviceNo |  |  |  |  | unscaled
06349 | [R] | EventTypeAndConditionLog50 |  |  |  |  | enum
06350 | [R] | EventTimeStampLog50HI |  |  |  |  | 1 s
06351 | [R] | EventTimeStampLog50LO
DATA LOG HEADER [R]
07001 | [R] | NoOfLogSeries |  |  |  |  | unscaled
07002 | [R] | LogSeries1ItemNo |  |  |  |  | unscaled
07003 | [R] | LogSeries1RegAddr |  |  |  |  | unscaled
07004 | [R] | LogSeries1SamplingTime |  |  |  |  | 1 s
07005 | [R] | LogSeries1NoOfSamples |  |  |  |  | unscaled
07006 | [R] | LogSeries2ItemNo |  |  |  |  | unscaled
07007 | [R] | LogSeries2RegAddr |  |  |  |  | unscaled
07008 | [R] | LogSeries2SamplingTime |  |  |  |  | 1 s
07009 | [R] | LogSeries2NoOfSamples |  |  |  |  | unscaled
… | [R] | LogSeries#ItemNo |  |  |  |  | unscaled
… | [R] | LogSeries#RegAddr |  |  |  |  | unscaled
… | [R] | LogSeries#SamplingTime |  |  |  |  | 1 s
… | [R] | LogSeries#NoOfSamples |  |  |  |  | unscaled
07254 | [R] | LogSeriesLItemNo |  |  |  |  | unscaled
07255 | [R] | LogSeriesLRegAddr |  |  |  |  | unscaled
07256 | [R] | LogSeriesLSamplingTime |  |  |  |  | 1 s
07257 | [R] | LogSeriesLNoOfSamples |  |  |  |  | unscaled
07258 | [R] | LogSeriesEndMark | Must be 0 |  |  |  | unscaled
DATA LOG SERIES [R]
07301 | [R] | LogSeries1ItemNo |  |  |  |  | unscaled
07302 | [R] | LogSeries1SamplingTime |  |  |  |  | 1 s
07303 | [R] | LogSeries1NoOfSamples |  |  |  |  | unscaled
07304 | [R] | LogSeries1TimeStampHI |  |  |  |  | 1 s
07305 | [R] | LogSeries1TimeStampLO
… | [R] | LogSeries1Sample1 |  |  |  |  | 0.01 m
:
| [R] | LogSeries1SampleN1 |  |  |  |  | 0.01 m
| [R] | LogSeries2ItemNo |  |  |  |  | unscaled
| [R] | LogSeries2SamplingTime |  |  |  |  | 1 s
| [R] | LogSeries2NoOfSamples |  |  |  |  | unscaled
| [R] | LogSeries2TimeStampHI |  |  |  |  | 1 s
| [R] | LogSeries2TimeStampLO
| [R] | LogSeries2Sample1 |  |  |  |  | 0.1 A
| [R] | :
| [R] | LogSeries2SampleN2 |  |  |  |  | 0.1 A
| [R] | LogSeries#ItemNo |  |  |  |  | unscaled
| [R] | LogSeries#SamplingTime |  |  |  |  | 1 s
| [R] | LogSeries#NoOfSamples |  |  |  |  | unscaled
| [R] | LogSeries#TimeStampHI |  |  |  |  | 1 s
| [R] | LogSeries#TimeStampLO
| [R] | LogSeries#Sample1 |  |  |  |  | 0.1 A
:
| [R] | LogSeries#SampleN# |  |  |  |  | 0.1 A
| [R] | LogSeriesLItemNo |  |  |  |  | unscaled
| [R] | LogSeriesLSamplingTime |  |  |  |  | 1 s
| [R] | LogSeriesLNoOfSamples |  |  |  |  | unscaled
| [R] | LogSeriesLTimeStampHI |  |  |  |  | 1 s
| [R] | LogSeriesLTimeStampLO
| [R] | LogSeriesLSample1 |  |  |  |  | 0.1 A
:
| [R] | LogSeriesLSampleNL |  |  |  |  | 0.1 A

## LC 2xx
GRUNDFOS CIM 200/260/500 MODBUS profile for LC 2xx controller
Sheet version: 02.11.00
Change date (d-m-y): 29-03-2023
All addresses are registers (16 bit), and the address is written in decimal format.
Reg. addr. | Access | Modbus parameter name | Modbus notes | Description | Bool/Enum description | Modbus Scale | Modbus Unit
CIM CONFIG [R/W] - All saved in EEPROM | [7 empty] | LC | SP
00001 | [R/W] | Config.SlaveMinimumReplyDelay | Saved in EEPROM | For adding a reply delay in ms (Modbus RTU only) |  | 1 | ms | x | x
00002 | [R/W] | RESERVED |  |  |  |  | unscaled | x | x
00003 | [R/W] | Config.SoftwareDefinedModbusAddress | Saved in EEPROM. If switch value is invalid, then use the value in this register as Modbus address. Make 0xE7 the default value. | Set a Modbus slave address to use if the address switches are set to an invalid value (Modbus RTU only). |  |  | unscaled | x | x
00004 | [R/W] | Config.SoftwareDefinedBitRate | Saved in EEPROM. Default = 4800. | If set to software defined, use this bit rate (Modbus RTU only). | 0 = 1200 1 = 2400 2 = 4800 3 = 9600 4 = 19200 5 = 38400 |  | enum | x | x
00005.0 | [R/W] | Config.AutoAckControlBits | Saved in EEPROM. 0 = Control bits are manually lowered. 1 = Control bits are automatically lowered, when module receives the event. (default) | Acknowlege behaviour of control bits | 0 = Manual, 1 = Automatic |  | bool | x | x
00006.0 | [R/W] | Config.ReadWriteSeparation | Saved in EEPROM. 0 = Registers are overwritten with values (default) 1 = Register readback is put into seperate registers | Separate reads from writes | 0 = No separation 1 = Separate registers |  | bool | x | x
00007 | [R/W] | Config.ScadaCallbackRegister | Register in the master used for unsolicited messages. CIM 250 SW handles EEPROM. | Register in the master used for unsolicited messages. (Cellular only) |  |  | unscaled | x | x
00008 | [R/W] | Config.NoDataActivityTimeout | The elapsed time with no data activity before the module issues a "GPRS restart". CIM 250 SW handles EEPROM. | The elapsed time with no data activity before the module issues a "connection restart". (Cellular only) |  | 1 | min | x | x
00009 | [R/W] | Config.SoftwareDefinedParity | Saved in EEPROM. Default value = 0. | If softwaredefined, use this parity setting (Modbus RTU only). | 0 = No parity 1 = Even parity 2 = Odd parity |  | enum | x | x
00010 | [R/W] | Config.SoftwareDefinedStopBit | Saved in EEPROM. Default value = 1. | If softwaredefined, use this stop bit setting (Modbus RTU only). | 0 = Not defined 1 = 1 stop bit 2 = 2 stop bit |  | enum | x | x
00011 | [R/W] | Config.ScadaPinCode | Code to use if ScadaPinCode is enabled. | Code to use if ScadaPinCode is enabled (Cellular only) |  |  |  | x | x
00013 | [R/W] | Config.GENIbusDiodeOff |  | Switching off the GENIbus diode (LED2) | 0=On (default) 1=Off |  | bool | x | x
CIM STATUS [R]
00021 | [R] | GENIbusCRCErrorCnt | GENIbus CRC err. | CRC error counter on the GENIbus |  |  | unscaled | x | x
00022 | [R] | GENIbusDataErrorCnt | GENIbus Data err. | Data error counter on the GENIbus |  |  | unscaled | x | x
00023 | [R] | CIMSoftwareVersionNumber | Shows version number | Software version number (CIM module firmware version) |  |  | unscaled | x | x
00024 | [R] | ActualModbusAddress | Shows actual address | Actual modbus slave address (Read only) |  |  | unscaled | x | x
00025 | [R] | GENIbusTXcount HI | GENIbus TX tlg count HI | Transmit counter on GENIbus |  |  | unscaled | x | x
00026 | [R] | GENIbusTXcount LO | GENIbus TX tlg count LO |  |  |  |  | x | x
00027 | [R] | GENIbusRXcount HI | GENIbus RX tlg count HI | Receive counter on GENIbus |  |  | unscaled | x | x
00028 | [R] | GENIbusRXcount LO | GENIbus RX tlg count LO |  |  |  |  | x | x
00029.0 | [R] | ScadaPinCodeEnabled |  | Determines if the use of a Scada Pin Code is enabled (Cellular only) | 0 = Pin code disabled 1 = Pin code enabled |  |  | x | x
00029.1 | [R] | WriteAccess |  | Determines if write (control) access is granted or not (Cellular only)+E115. | 0 = No write access 1 = Write access |  |  | x | x
00030 | [R] | Unit Family | Grundfos specific | Grundfos product family | 0 = - 1 = UPE/MAGNA pump 2 = MGE 7 = Motor Protection Unit 17 = Multi-E 21 = MPC / Multi-B 25 = CU 351 - CR Monitor 26 = CU 36x - Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller 48 = Level Controller LC 2x1 255 = N/A |  | enum | x | x
00031 | [R] | Unit Type | Grundfos specific | Grundfos product type |  |  | unscaled | x | x
00032 | [R] | Unit Version | Grundfos specific | Grundfos product version |  |  | unscaled | x | x
00033 | [R] | BatteryState | Equal to gsm_battery_state (5, 52) | State of CIM module battery (Cellular only) | 0 = Battery not present 1 = Battery must be replaced 2 = Battery charging 3 = Battery needs charging, but temperature too high 4 = Battery needs charging, but temperature too low 5 = Battery Low 6 = Battery OK 255 = Battery state not available |  | enum | x | x
00034 | [R] | ProductSoftwareVersionHI | From ASCII string | Product software version (BCD digit 1-4 aa.bb) |  |  | BCD number | x | x
00035 | [R] | ProductSoftwareVersionLO | From ASCII string | Product software version (BCD digit 5-8 cc.dd) |  |  | BCD number | x | x
00036 | [R] | ProductSoftwareDayMonth | From ASCII string | Product software date (BCD ddmm) |  |  | BCD number | x | x
00037 | [R] | ProductSoftwareYear | From ASCII string | Product software date (BCD yyyy) |  |  | BCD number | x | x
CONTROL AND SETTINGS [W]
00101.0 | [W] | SystemControl.ResetAlarm | Rising edge | Reset Alarm | 0 = No resetting 1 = Reset alarm |  | bool | x | x
00101.2 | [W] | SystemControl.ResetEventLog | Rising edge | Reset event log | 0 = No resetting 1 = Reset event log |  | bool | x | x
00101.3 | [W] | SystemControl.Interlock | Rising edge | Interlock command | 0 = No command 1 = Interlock System |  | bool
00101.4 | [W] | SystemControl.Auto | Rising edge | Auto command | 0 = No command 1 = Set System to Auto |  | bool
00103 | [W] | Pump1Control | On value change | Manual control of pump 1 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum | x | x
00104 | [W] | Pump2Control | On value change | Manual control of pump 2 | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum | x | x
00110 | [W] | SetEventLogClearID | On value change | Selects last record in event log record to clear |  |  | unscaled | x | x
00112 | [W] | SetRealTimeClockHI | On value change | Set Real Time Clock (32 bit UNIX format) high order |  | 1 | s |  | x
00113 | [W] | SetRealTimeClockLO | On value change | Set Real Time Clock (32 bit UNIX format) low order. This triggers the update. |  |  | s |  | x
00114 | [W] | SetRtcSecond |  | Set Real Time Clock (Seconds) |  |  | enum |  | x
00115 | [W] | SetRtcMinute |  | Set Real Time Clock (Minutes) |  |  | enum |  | x
00116 | [W] | SetRtcHour |  | Set Real Time Clock (Hours) |  |  | enum |  | x
00117 | [W] | SetRtcDay |  | Set Real Time Clock (Day) |  |  | enum |  | x
00118 | [W] | SetRtcMonth |  | Set Real Time Clock (Month) |  |  | enum |  | x
00119 | [W] | SetRtcYear |  | Set Real Time Clock (Year - after 2000) |  |  | enum |  | x
00120.0 | [W] | SetRtc |  | Set Real Time Clock (Trigger of normal format) |  |  | bool |  | x
00121 | [W] | SetOverFlowLevel | On value change | Set over flow level |  | 0.01 | m
00122 | [W] | SetHighLevel | On value change | Set high level |  | 0.01 | m | x | x
00123 | [W] | SetAlarmLevel | On value change | Set alarm level |  | 0.01 | m
00124 | [W] | SetDryRunningLevel | On value change | Set dry running level |  | 0.01 | m | x | x
00125 | [W] | SetFoamDrainingLevel | On value change | Set foam draining level |  | 0.01 | m
00126 | [W] | SetStartLevelPump1 | On value change | Set start level pump 1 |  | 0.01 | m | x | x
00127 | [W] | SetStopLevelPump1 | On value change | Set stop level pump1 |  | 0.01 | m | x | x
00128 | [W] | SetStartLevelPump2 | On value change | Set start level pump 2 |  | 0.01 | m | x | x
00129 | [W] | SetStopLevelPump2 | On value change | Set stop level pump 2 |  | 0.01 | m
STATUS [R]
00201.0 | [R] | Acknowledge.ResetAlarm | 1 = Acknowledged | Acknowledge of Reset Alarm command | 0 = No acknowledge 1 = Acknowledged |  | bool | x | x
00201.1 | [R] | Acknowledge.SetRtc | 1 = Acknowledged | Acknowledge of Set Real Time Clock command | 0 = No acknowledge 1 = Acknowledged |  | bool |  | x
00201.2 | [R] | Acknowledge.ResetEventLog | 1 = Acknowledged | Acknowledge of Reset Event Log command | 0 = No acknowledge 1 = Acknowledged |  | bool | x | x
00201.3 | [R] | Acknowledge.Interlock | 1 = Acknowledged | Acknowledge of Interlock command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.4 | [R] | Acknowledge.Auto | 1 = Acknowledged | Acknowledge of Auto command | 0 = No acknowledge 1 = Acknowledged |  | bool
00202.1 | [R] | Status.Alarm |  | Presence of an alarm in LC controller | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00202.2 | [R] | Status.Warning |  | Presence of a warning in LC controller | 0 = No warning 1 = Warning present |  | bool | x | x
00202.3 | [R] | Status.ManualControl |  | Manual or auto control | 0 = Auto control 1 = Manual control |  | bool | x | x
00203 | [R] | OperatingMode |  | Actual system operating mode | 0 = Standby 1 = Start-up delay 2 = Pumping 3 = Stop delay 4 = Pumping max 5 = Stopped 8 = Pump anti seizing 9 = Manual control 12 = Level sensor error 13 = All pumps in alarm 14 = All pumps out of operation |  | enum | x | x
00204.0 | [R] | PumpsPresent.Pump1 | Bit interpreted, 1 = Present | Presence of pump 1 | 0 = Not present 1 = Present |  | bool | x | x
00204.1 | [R] | PumpsPresent.Pump2 | Bit interpreted, 1 = Present | Presence of pump 2 | 0 = Not present 1 = Present |  | bool | x | x
00205.0 | [R] | PumpsDisabled.Pump1 | Bit interpreted, 1 = Disabled | Enabled/Disabled status of pump 1 | 0 = Enabled 1 = Disabled |  | bool
00205.1 | [R] | PumpsDisabled.Pump2 | Bit interpreted, 1 = Disabled | Enabled/Disabled status of pump 2 | 0 = Enabled 1 = Disabled |  | bool
00206.0 | [R] | PumpsRunning.Pump1 | Bit interpreted, 1 = Running | Rotation status of pump 1 | 0 = Not running (or not present) 1 = Running |  | bool | x | x
00206.1 | [R] | PumpsRunning.Pump2 | Bit interpreted, 1 = Running | Rotation status of pump 2 | 0 = Not running (or not present) 1 = Running |  | bool | x | x
00207.0 | [R] | PumpsMonitoringFault.Pump1 | Bit interpreted, 1 = Monitor Fault | Monitoring fault on pump 1 | 0 = No monitoring fault 1 = Monitoring fault |  | bool | x | x
00207.1 | [R] | PumpsMonitoringFault.Pump2 | Bit interpreted, 1 = Monitor Fault | Monitoring fault on pump 2 | 0 = No monitoring fault 1 = Monitoring fault |  | bool | x | x
00208.0 | [R] | PumpsWarning.Pump1 | Bit interpreted, 1 = Warning | Warning on pump 1 | 0 = No warning 1 = Warning |  | bool | x | x
00208.1 | [R] | PumpsWarning.Pump2 | Bit interpreted, 1 = Warning | Warning on pump 2 | 0 = No warning 1 = Warning |  | bool | x | x
00209.0 | [R] | PumpsAlarm.Pump1 | Bit interpreted, 1 = Fault | Alarm on pump 1 | 0 = No alarm 1 = Fault |  | bool | x | x
00209.1 | [R] | PumpsAlarm.Pump2 | Bit interpreted, 1 = Fault | Alarm on pump 2 | 0 = No alarm 1 = Fault |  | bool | x | x
00210.1 | [R] | SystemAlarms1.High level alarm |  | High level alarm (191) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00210.3 | [R] | SystemAlarms1.Dry running |  | Dry running alarm (57) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00210.5 | [R] | SystemAlarms1.Float switch sequence inconsistency |  | Float switch sequence inconsistency (205) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00210.11 | [R] | SystemAlarms1.Distributed I/O module comm. Fault |  | I/O module communication alarm (226) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00211.13 | [R] | SystemAlarms2.AI sensor 1 signal fault |  | AI sensor 1 signal fault alarm (165) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00212.3 | [R] | SystemAlarms3.UserEvent1 |  | User event 1 alarm (249) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00212.4 | [R] | SystemAlarms3.UserEvent2 |  | User event 2 alarm (250) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00212.8 | [R] | SystemAlarms3.LimitExceded1 |  | Limit exceded sensor 1 alarm (94) | 0 = No Alarm 1 = Alarm present |  | bool |  | x
00212.9 | [R] | SystemAlarms3.LimitExceded2 |  | Limit exceded sensor 2 alarm (95) | 0 = No Alarm 1 = Alarm present |  | bool |  | x
00212.10 | [R] | SystemAlarms3.ExternalFaultSignal |  | External fault signal alarm (3)] | 0 = No Alarm 1 = Alarm present |  | bool |  | x
00212.14 | [R] | SystemAlarms3.InternalCommFailure |  | Internal communication failure (76) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00212.15 | [R] | SystemAlarms3.SetupConflict |  | Setup conflict (25) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00213.12 | [R] | SystemWarnings1.Add-on CIM comm. Fault |  | Fault in connection between controller and CIM module (159) | 0 = No warning 1 = Warning present |  | bool | x | x
00214.0 | [R] | SystemWarnings2.Battery/UPS fault |  | Battery warning (248) | 0 = No warning 1 = Warning present |  | bool | x | x
00215.1 | [R] | SystemWarnings3.WaterOnFloor |  | Water on floor warning (229) | 0 = No warning 1 = Warning present |  | bool | x | x
00215.3 | [R] | SystemWarnings3.UserEvent1 |  | User event 1 warning (249) | 0 = No warning 1 = Warning present |  | bool | x | x
00215.4 | [R] | SystemWarnings3.UserEvent2 |  | User event 2 warning (250) | 0 = No warning 1 = Warning present |  | bool | x | x
00215.8 | [R] | SystemWarnings3.LimitExceded1 |  | Limit exceded sensor 1 warning (94) | 0 = No warning 1 = Warning present |  | bool |  | x
00215.9 | [R] | SystemWarnings3.LimitExceded2 |  | Limit exceded sensor 2 warning (95) | 0 = No warning 1 = Warning present |  | bool |  | x
00215.10 | [R] | SystemWarnings3.ExternalFaultSignal |  | External fault signal warning (3) | 0 = No warning 1 = Warning present |  | bool
00215.12 | [R] | SystemWarnings3.Intrusion |  | Intrusion (Door opened) (117) | 0 = No warning 1 = Warning present |  | bool | x | x
00215.13 | [R] | SystemWarnings3.MemoryAccessError |  | Memory access error (84) | 0 = No warning 1 = Warning present |  | bool | x | x
00216 | [R] | EventLogLatestID |  | Latest ID of event log |  |  | unscaled | x | x
00217 | [R] | NumberOfFloatSwitches |  | Amount of float switches in system |  |  | unscaled | x | x
00218.0 | [R] | FloatSwitchesStatus.Switch1 |  | Status of float switch 1 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool | s | s
00218.1 | [R] | FloatSwitchesStatus.Switch2 |  | Status of float switch 2 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool | s | s
00218.2 | [R] | FloatSwitchesStatus.Switch3 |  | Status of float switch 3 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool | s | s
00218.3 | [R] | FloatSwitchesStatus.Switch4 |  | Status of float switch 4 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool | s | s
00218.4 | [R] | FloatSwitchesStatus.Switch5 |  | Status of float switch 5 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool | s | s
00219 | [R] | FloatSwitch1Function |  | Function of float switch 1 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum | x | x
00220 | [R] | FloatSwitch2Function |  | Function of float switch 2 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum | x | x
00221 | [R] | FloatSwitch3Function |  | Function of float switch 3 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum | x | x
00222 | [R] | FloatSwitch4Function |  | Function of float switch 4 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum | x | x
00223 | [R] | FloatSwitch5Function |  | Function of float switch 5 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum | x | x
00224.0 | [R] | Sensors.LevelControlSensor |  | Presence of level sensor for control | 0 = Sensor not present 1 = Sensor present |  | bool | x | x
00224.1 | [R] | Sensors.PressureControlSensor |  | Presence of pressure level sensor (for control) | 0 = Sensor not present 1 = Sensor present |  | bool | x | x
00224.2 | [R] | Sensors.FloatSwithces |  | Presence of float switches for control | 0 = Float switches not present 1 = Float Switches present |  | bool | x | x
00224.3 | [R] | Sensors.FlowSensor |  | Presence of flow sensor | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.4 | [R] | Sensors.Power/EnergySensor |  | Presence of power/energy sensor | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.5 | [R] | Sensors.UserDefinedAIsensor1present |  | Presence of AI sensor 1 | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.6 | [R] | Sensors.UserDefinedAIsensor2present |  | Presence of AI sensor 2 | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.7 | [R] | Sensors.UserDefinedAIsensor3present |  | Presence of AI sensor 3 | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.8 | [R] | Sensors.UserDefinedAIsensor4present |  | Presence of AI sensor 4 | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.9 | [R] | Sensors.UserDefinedAIsensor5present |  | Presence of AI sensor 5 | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.10 | [R] | Sensors.TurbiditySensor |  | Presence of turbidity sensor | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.11 | [R] | Sensors.PHSensor |  | Presence of PH sensor | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.12 | [R] | Sensors.ConductivitySensor |  | Presence of conductivity sensor | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.13 | [R] | Sensors.PulseFlowMeter |  | Presence of pulse flow meter | 0 = Flow meter not present 1 = Flow meter present |  | bool |  | x
00224.14 | [R] | Sensors.PressureSensor |  | Presence of pressure sensor | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00224.15 | [R] | Sensors.LevelSensor |  | Presence of level sensor | 0 = Sensor not present 1 = Sensor present |  | bool |  | x
00228 | [R] | UNIXRealTimeClockHI |  | Real Time Clock (32 bit UNIX format) |  | 1 | s |  | x
00229 | [R] | UNIXRealTimeClockLO | [6 empty] | x
00230 | [R] | RtcSecond |  | Real Time Clock (Seconds) |  |  | enum |  | x
00231 | [R] | RtcMinute |  | Real Time Clock (Minutes) |  |  | enum |  | x
00232 | [R] | RtcHour |  | Real Time Clock (Hours) |  |  | enum |  | x
00233 | [R] | RtcDay |  | Real Time Clock (Day) |  |  | enum |  | x
00234 | [R] | RtcMonth |  | Real Time Clock (Month) |  |  | enum |  | x
00235 | [R] | RtcYear |  | Real Time Clock (Year) |  |  | enum |  | x
00236 | [R] | CellularSignalLevelActual |  | Actual Cellular signal level |  | 1 | % | x | x
00237 | [R] | CellularSignalLevelAverage |  | Average Cellular signal level |  | 1 | % | x | x
00238 | [R] | IPAddressHI |  | IP address (as a value) |  |  | IP | x | x
00239 | [R] | IPAddressLO |  |  |  |  | IP | x | x
00240 | [R] | OverFlowLevel |  | Actual overflow level |  | 0.01 | m
00241 | [R] | HighLevel |  | Actual high level |  | 0.01 | m | x | x
00242 | [R] | AlarmLevel |  | Actual alarm level |  | 0.01 | m
00243 | [R] | DryRunningLevel |  | Actual dry running level |  | 0.01 | m | x | x
00244 | [R] | FoamDrainingLevel |  | Actual foam draining level |  | 0.01 | m
00245 | [R] | StartLevelPump1 |  | Actual start level of pump 1 |  | 0.01 | m | x | x
00246 | [R] | StopLevelPump1 |  | Actual stop level of pump 1 |  | 0.01 | m | x | x
00247 | [R] | StartLevelPump2 |  | Actual start level of pump 2 |  | 0.01 | m | x | x
00248 | [R] | StopLevelPump2 |  | Actual stop level of pump 2 |  | 0.01 | m
00272.0 | [R] | SystemAlarms5.PerformanceRequirementNotMet |  | Performance requirement cannot be met (17) | 0 = No Alarm 1 = Alarm present |  | bool
00272.1 | [R] | SystemAlarms5.ExternalWarningSignal |  | External warning signal (46) | 0 = No Alarm 1 = Alarm present |  | bool
00272.2 | [R] | SystemAlarms5.CableTheft |  | Missing Cable detected, cable theft (130) | 0 = No Alarm 1 = Alarm present |  | bool
00272.3 | [R] | SystemAlarms5.RealTimeClockOutOfOrder |  | Real time clock out of order alarm (157) | 0 = No Alarm 1 = Alarm present |  | bool
00272.4 | [R] | SystemAlarms5.SpecificEnergyHigh |  | Operation with reduced efficiency, specific energy high (196) | 0 = No Alarm 1 = Alarm present |  | bool
00272.5 | [R] | SystemAlarms5.LevelSettingsInvalid |  | Start or stop level setting invalid or missing (25.1009) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00272.6 | [R] | SystemAlarms5.Missing AnalogLevelSetting |  | Analog level sensor not configured (25.1010) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00272.7 | [R] | SystemAlarms5.DublicateSwitchSetting |  | Dublicateswitch setting (25.1011) | 0 = No Alarm 1 = Alarm present |  | bool | x | x
00272.8 | [R] | SystemAlarms5.OperatingOnBatteryBackup |  | Operating on battery backup (142) | 0 = No Alarm 1 = Alarm present |  | bool
00273.0 | [R] | SystemWarnings5.PerformanceRequirementNotMet |  | Performance requirement cannot be met (17) | 0 = No warning 1 = Warning present |  | bool |  | x
00273.1 | [R] | SystemWarnings5.ExternalWarningSignal |  | External warning signal (46) | 0 = No warning 1 = Warning present |  | bool |  | x
00273.2 | [R] | SystemWarnings5.CableTheft |  | Missing Cable detected, cable theft (130) | 0 = No warning 1 = Warning present |  | bool |  | x
00273.3 | [R] | SystemWarnings5.RealTimeClockOutOfOrder |  | Real time clock out of order warning (157) | 0 = No warning 1 = Warning present |  | bool | x | x
00273.4 | [R] | SystemWarnings5.SpecificEnergyHigh |  | Operation with reduced efficiency, specific energy high (196) | 0 = No warning 1 = Warning present |  | bool
00273.5 | [R] | SystemWarnings5.LevelSettingsInvalid |  | Start or stop level setting invalid or missing (25.1009) | 0 = No warning 1 = Warning present |  | bool
00273.6 | [R] | SystemWarnings5.Missing AnalogLevelSetting |  | Analog level sensor not configured (25.1010) | 0 = No warning 1 = Warning present |  | bool
00273.7 | [R] | SystemWarnings5.DublicateSwitchSetting |  | Dublicateswitch setting (25.1011) | 0 = No warning 1 = Warning present |  | bool
00273.8 | [R] | SystemWarning5.OperatingOnBatteryBackup |  | Operating on battery backup (142) | 0 = No warning 1 = Warning present |  | bool |  | x
00274 | [R] | AnalogIn1Min |  | Sensor range minimum |  |  | unit |  | s
00275 | [R] | AnalogIn1Max |  | Sensor range maximum |  |  | unit |  | s
00276 | [R] | AnalogIn1Unit |  | Sensor unit |  |  | enum |  | s
00277 | [R] | AnalogIn2Min |  | Sensor range minimum |  |  | unit |  | s
00278 | [R] | AnalogIn2Max |  | Sensor range maximum |  |  | unit |  | s
00279 | [R] | AnalogIn2Unit |  | Sensor unit |  |  | enum |  | s
00280 | [R] | AnalogIn3Min |  | Sensor range minimum |  |  | unit |  | s
00281 | [R] | AnalogIn3Max |  | Sensor range maximum |  |  | unit |  | s
00282 | [R] | AnalogIn3Unit |  | Sensor unit |  |  | enum |  | s
00283 | [R] | AnalogIn4Min |  | Sensor range minimum |  |  | unit |  | s
00284 | [R] | AnalogIn4Max |  | Sensor range maximum |  |  | unit |  | s
00285 | [R] | AnalogIn4Unit |  | Sensor unit |  |  | enum |  | s
00286 | [R] | AnalogIn5Min |  | Sensor range minimum |  |  | unit |  | s
00287 | [R] | AnalogIn5Max |  | Sensor range maximum |  |  | unit |  | s
00288 | [R] | AnalogIn5Unit |  | Sensor unit |  |  | enum |  | s
SYSTEM DATA [R]
00301 | [R] | SystemWaterLevel |  | System water level |  | 0.01 | m | s | s
00308 | [R] | SystemPowerHI |  | System power consumption |  | 1 | W | x | x
00309 | [R] | SystemPowerLO | [5 empty] | x | x
00310 | [R] | SystemEnergyHI |  | System energy consumption |  | 0.1 | kWh | x | x
00311 | [R] | SystemEnergyLO | [5 empty] | x | x
00312 | [R] | SystemEnergyYesterday |  | System energy comsumption yesterday |  | 0.1 | kWh | x | x
00313 | [R] | SystemEnergyToday |  | System energy comsumption today |  | 0.1 | kWh | x | x
00323 | [R] | PitOverflowTime |  | Overflow time |  | 1 | min | x
00324 | [R] | PitOverflowTimeYesterday |  | Overflow time yesterday |  | 1 | min | x
00325 | [R] | PitOverflowTimeToday |  | Overflow time today |  | 1 | min | x
00326 | [R] | PitOverflowCounter |  | Number of overflows |  |  | unscaled | x
00327 | [R] | PitOverflowCounterYesterday |  | Number of overflows yesterday |  |  | unscaled | x
00328 | [R] | PitOverflowCounterToday |  | Number of overflows today |  |  | unscaled | x
00329 | [R] | SystemOperatingTimeHI |  | System operating time |  | 1 | min | x | x
00330 | [R] | SystemOperatingTimeLO | [5 empty] | x | x
00331 | [R] | System2PumpsOprTimeHI |  | 2 pumps operating time |  | 1 | min
00332 | [R] | System2PumpsOprTimeLO |  |  |  |  | min
00333 | [R] | System2PumpsOprTimeYesterday |  | 2 pumps operating time yesterday |  | 1 | min
00334 | [R] | System2PumpsOprTimeToday |  | 2 pumps operating time today |  | 1 | min
00351 | [R] | UserAnalogInput1 |  | User analog input 1 |  | 0.1 | % | x | x
00352 | [R] | UserAnalogInput2 |  | User analog input 2 |  | 0.1 | % | x | x
00353 | [R] | UserAnalogInput3 |  | User analog input 3 |  | 0.1 | % | x | x
00354 | [R] | System0PumpsOprTimeHI |  | 0 pumps operating time |  | 1 | min
00355 | [R] | System0PumpsOprTimeLO
00356 | [R] | System0PumpsOprTimeYesterday |  | 0 pumps operating time yesterday |  | 1 | min
00357 | [R] | System0PumpsOprTimeToday |  | 0 pumps operating time today |  | 1 | min
00358 | [R] | System1PumpsOprTimeHI |  | 1 pump operating time |  | 1 | min
00359 | [R] | System1PumpsOprTimeLO
00360 | [R] | System1PumpsOprTimeYesterday |  | 1 pumps operating time yesterday |  | 1 | min
00361 | [R] | System1PumpsOprTimeToday |  | 1 pumps operating time today |  | 1 | min
00391 | [R] | UserDigitalInBlock1 |  | User digital inputs 15-0 |  |  | unscaled | x | x
00392 | [R] | UserDigitalInBlock2 |  | User digital inputs 31-16 |  |  | unscaled |  | x
00393 | [R] | UserDigitalOutput |  | User digital outputs |  |  | unscaled | x | x
00394 | [R] | UserAnalogInput4 |  | User analog input 4 |  | 0.1 | % | x | x
00395 | [R] | UserAnalogInput5 |  | User analog input 5 |  | 0.1 | % | x | x
00396 | [R] | PulseFlowMeter |  | Flow value measured with pulse flow meter input |  | 0.1 | ltr/s |  | s
00397 | [R] | Turbidity |  | Cloudiness of a fluid by small particles |  | 0.1 | NTU |  | s
00398 | [R] | PhMeasure |  | Measure of acidity or alkalinity |  | 0.01 | PH |  | s
00399 | [R] | Conductivity |  | An electrolyte solutuions ability to conduct electricity |  | 1 | uS/cm |  | s
PUMP 1 [R]
00401.0 | [R] | Pump1Status.Presence |  | Presence of pump 1 | 0 = No present 1 = Present |  | bool | x | x
00401.1 | [R] | Pump1Status.Running |  | Rotation status of pump 1 | 0 = No rotation 1 = Rotation |  | bool | x | x
00401.3 | [R] | Pump1Status.Warning |  | Warning status of pump 1 | 0 = No warning 1 = Warning |  | bool | x | x
00401.4 | [R] | Pump1Status.Alarm |  | Alarm status of pump 1 | 0 = No alarm 1 = Alarm |  | bool | x | x
00401.11 | [R] | Pump1Status.PumpDisabled |  | Enabled/Disabled status of pump 1 | 0 = Enabled 1 = Disabled |  | bool
00402 | [R] | Pump1ControlSource |  | Control source of pump 1 | 0 = Auto 1 = Manual by switch 2 = Manual by display 3 = Manual from bus 255 = - |  | enum | x | x
00403 | [R] | Pump1ConnectionType |  | Connection type of pump 1 | 0 = Pump connected to wall mounted controller or not present 1 = Pump connected via pump module 255 = - |  | enum | x | x
00404 | [R] | Pump1OprTimeHI |  | Operating time of pump 1 |  | 1 | min | x | x
00405 | [R] | Pump1OprTimeLO | [5 empty] | x | x
00406 | [R] | Pump1TimeToServiceHI |  | Time to service for pump 1 |  | 1 | min | x | x
00407 | [R] | Pump1TimeToServiceLO |  |  |  |  | min | x | x
00408 | [R] | Pump1OprTimeYesterday |  | Operating time yesterday, pump 1 |  | 1 | min | x | x
00409 | [R] | Pump1OprTimeToday |  | Operating time today, pump 1 |  | 1 | min |  | x
00410 | [R] | Pump1LatestOprTime |  | Latest operating time for pump 1 |  | 1 | s | x | x
00411 | [R] | Pump1StartCounterHI |  | Start counter for pump 1 |  |  | unscaled | x | x
00412 | [R] | Pump1StartCounterLO |  |  |  |  | unscaled | x | x
00413 | [R] | Pump1StartCounterYesterday |  | Start counter yesterday, pump 1 |  |  | unscaled | x | x
00414 | [R] | Pump1StartCounterToday |  | Start counter today, pump 1 |  |  | unscaled |  | x
00415 | [R] | Pump1StartsPerHour |  | Number of starts within the latest hour, pump 1 |  |  | unscaled | x | x
00418 | [R] | Pump1Current |  | Motor current, pump 1 |  | 0.1 | A | x | x
00419 | [R] | Pump1LatestCurrent |  | Latest motor current, pump 1 |  | 0.1 | A | x | x
00420 | [R] | Pump1Voltage |  | Motor voltage, pump 1 |  | 0.1 | V | x | x
00423.0 | [R] | Pump1Alarms1.MotorTemp.alarmPTC1 |  | Motor temperature PTC1 alarm (69) | 0 = No alarm 1 = Alarm |  | bool | x | x
00423.7 | [R] | Pump1Alarms1.MotorLowVoltage |  | Motor voltage low (40) | 0 = No alarm 1 = Alarm |  | bool | x | x
00423.8 | [R] | Pump1Alarms1.MotorHighVoltage |  | Motor voltage high (32) | 0 = No alarm 1 = Alarm |  | bool | x | x
00423.9 | [R] | Pump1Alarms1.MotorPhaseSequenceReversal |  | Motor phase sequence reversed (9) | 0 = No alarm 1 = Alarm |  | bool | x | x
00423.10 | [R] | Pump1Alarms1.MotorOverload |  | Motor overload (48) | 0 = No alarm 1 = Alarm |  | bool | x | x
00423.11 | [R] | Pump1Alarms1.MotorUnderload |  | Motor underload (56) | 0 = No alarm 1 = Alarm |  | bool | x | x
00423.13 | [R] | Pump1Alarms1.MotorMissingPhase |  | Motor missing phase (2) | 0 = No alarm 1 = Alarm |  | bool | x | x
00423.15 | [R] | Pump1Alarms1.LoadContinuesDespiteMotorRelayisOff |  | Load continues, but motor relay is off (26) | 0 = No alarm 1 = Alarm |  | bool | x | x
00424.2 | [R] | Pump1Alarms2.MotorMoistureSwitch |  | Motor moisture (22) | 0 = No alarm 1 = Alarm |  | bool | x | x
00424.6 | [R] | Pump1Alarms2.MotorContactorFeedbackFault |  | Motor contactor feedback fault (220) | 0 = No alarm 1 = Alarm |  | bool | x | x
00424.7 | [R] | Pump1Alarms2.MotorMaxStartsPerHour |  | Motor max starts per hour limit exceeded (21) | 0 = No alarm 1 = Alarm |  | bool | x | x
00424.9 | [R] | Pump1Alarms2.TooManyPumpAuto-restarts |  | Too many auto restarts of pump (4) | 0 = No alarm 1 = Alarm |  | bool | x | x
00424.14 | [R] | Pump1Alarms2.ParameterVerificatonErrEEPROM |  | EEPROM error in parameter area (85) | 0 = No alarm 1 = Alarm |  | bool | x | x
00424.15 | [R] | Pump1Alarms2.DriveProtectMeasFault |  | Motor drive protection measurement fault (163) | 0 = No alarm 1 = Alarm |  | bool | x | x
00425.1 | [R] | Pump1.Alarms3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump module communication (225) | 0 = No alarm 1 = Alarm |  | bool | x | x
00425.4 | [R] | Pump1.Alarms3.PTCSensorSignalFault |  | PTC sensor fault (181) | 0 = No alarm 1 = Alarm |  | bool | x | x
00425.9 | [R] | Pump1.Alarms3.SetupConflict |  | Conflict in setup parameters for current measurement (163) | 0 = No alarm 1 = Alarm |  | bool | x | x
00425.10 | [R] | Pump1.Alarms3.GeneralHardwareFault |  | General hardware fault (72) | 0 = No alarm 1 = Alarm |  | bool | x | x
00426.7 | [R] | Pump1Warnings1.MotorLowVoltage |  | Motor voltage low | 0 = No warning 1 = Warning |  | bool | x | x
00426.8 | [R] | Pump1Warnings1.MotorHighVoltage |  | Motor voltage high | 0 = No warning 1 = Warning |  | bool | x | x
00426.15 | [R] | Pump1Warnings1.LoadContinuesDespiteMotorRelayIsOff |  | Load continues, but motor relay is off (26) | 0 = No warning 1 = Warning |  | bool | x | x
00427.7 | [R] | Pump1Warnings2.MotorMaxStartsPerHour |  | Motor max starts per hour limit exceeded (21) | 0 = No warning 1 = Warning |  | bool | x | x
00427.8 | [R] | Pump1Warnings2.MotoroperatingtimeserviceLimitExceeded |  | Motor service time exceeded (12) | 0 = No warning 1 = Warning |  | bool | x | x
00428.4 | [R] | Pump1.Warnings3.PTCSensorSignalFault |  | PTC sensor signal fault (181) | 0 = No warning 1 = Warning |  | bool | x | x
00431 | [R] | Pump1PowerHI |  | Power consumption, pump 1 |  | 1 | W | x | x
00432 | [R] | Pump1PowerLO | [5 empty] | x | x
00433 | [R] | Pump1EnergyHI |  | Energy consumption, pump 1 |  | 0.1 | kWh | x | x
00434 | [R] | Pump1EnergyLO | [5 empty] | x | x
00435 | [R] | Pump1CosPhi |  | Motor cosine phi, pump 1 (latched value) |  | 0.01 |  | x | x
PUMP 2 [R]
00451.0 | [R] | Pump2Status.Presence |  | Presence of pump 2 | 0 = No present 1 = Present |  | bool | x | x
00451.1 | [R] | Pump2Status.Running |  | Rotation status of pump 2 | 0 = No rotation 1 = Rotation |  | bool | x | x
00451.3 | [R] | Pump2Status.Warning |  | Warning status of pump 2 | 0 = No warning 1 = Warning |  | bool | x | x
00451.4 | [R] | Pump2Status.Alarm |  | Alarm status of pump 2 | 0 = No alarm 1 = Alarm |  | bool | x | x
00451.11 | [R] | Pump2Status.PumpDisabled |  | Enabled/Disabled status of pump 2 | 0 = Enabled 1 = Disabled |  | bool
00452 | [R] | Pump2ControlSource |  | Control source of pump 2 | 0 = Auto 1 = Manual by switch 2 = Manual by display 3 = Manual from bus 255 = - |  | enum | x | x
00453 | [R] | Pump2ConnectionType |  | Connection type of pump 2 | 0 = Pump connected to wall mounted controller or not present 1 = Pump connected via pump module 255 = - |  | enum | x | x
00454 | [R] | Pump2OprTimeHI |  | Operating time of pump 2 |  | 1 | min | x | x
00455 | [R] | Pump2OprTimeLO | [5 empty] | x | x
00456 | [R] | Pump2TimeToServiceHI |  | Time to service for pump 2 |  | 1 | min | x | x
00457 | [R] | Pump2TimeToServiceLO | [5 empty] | x | x
00458 | [R] | Pump2OprTimeYesterday |  | Operating time yesterday, pump 2 |  | 1 | min | x | x
00459 | [R] | Pump2OprTimeToday |  | Operating time today, pump 2 |  | 1 | min |  | x
00460 | [R] | Pump2LatestOprTime |  | Latest operating time for pump 2 |  | 1 | s | x | x
00461 | [R] | Pump2StartCounterHI |  | Start counter for pump 2 |  |  | unscaled | x | x
00462 | [R] | Pump2StartCounterLO | [5 empty] | x | x
00463 | [R] | Pump2StartCounterYesterday |  | Start counter yesterday, pump 2 |  |  | unscaled | x | x
00464 | [R] | Pump2StartCounterToday |  | Start counter today, pump 2 |  |  | unscaled |  | x
00465 | [R] | Pump2StartsPerHour |  | Number of starts within the latest hour, pump 2 |  |  | unscaled | x | x
00468 | [R] | Pump2Current |  | Motor current, pump 2 |  | 0.1 | A | x | x
00469 | [R] | Pump2LatestCurrent |  | Latest motor current, pump 2 |  | 0.1 | A | x | x
00470 | [R] | Pump2Voltage |  | Motor voltage, pump 2 |  | 0.1 | V | x | x
00473.0 | [R] | Pump2Alarms1.MotorTemp.alarmPTC1 |  | Motor temperature PTC1 alarm (69) | 0 = No alarm 1 = Alarm |  | bool | x | x
00473.7 | [R] | Pump2Alarms1.MotorLowVoltage |  | Motor voltage low (40) | 0 = No alarm 1 = Alarm |  | bool | x | x
00473.8 | [R] | Pump2Alarms1.MotorHighVoltage |  | Motor voltage high (32) | 0 = No alarm 1 = Alarm |  | bool | x | x
00473.9 | [R] | Pump2Alarms1.MotorPhaseSequenceReversal |  | Motor phase sequence reversed (9) | 0 = No alarm 1 = Alarm |  | bool | x | x
00473.10 | [R] | Pump2Alarms1.MotorOverload |  | Motor overload (48) | 0 = No alarm 1 = Alarm |  | bool | x | x
00473.11 | [R] | Pump2Alarms1.MotorUnderload |  | Motor underload (56) | 0 = No alarm 1 = Alarm |  | bool | x | x
00473.13 | [R] | Pump2Alarms1.MotorMissingPhase |  | Motor missing phase (2) | 0 = No alarm 1 = Alarm |  | bool | x | x
00473.15 | [R] | Pump2Alarms1.LoadContinuesDespiteMotorRelayisOff |  | Load continues, but motor relay is off | 0 = No alarm 1 = Alarm |  | bool | x | x
00474.2 | [R] | Pump2Alarms2.MotorMoistureSwitch |  | Motor moisture (22) | 0 = No alarm 1 = Alarm |  | bool | x | x
00474.6 | [R] | Pump2Alarms2.MotorContactorFeedbackFault |  | Motor contactor feedback | 0 = No alarm 1 = Alarm |  | bool | x | x
00474.7 | [R] | Pump2Alarms2.MotorMaxStartsPerHour |  | Motor max starts per hour limit exceeded (21) | 0 = No alarm 1 = Alarm |  | bool | x | x
00474.9 | [R] | Pump2Alarms2.TooManyPumpAuto-restarts |  | Too many auto restarts of pump (4) | 0 = No alarm 1 = Alarm |  | bool | x | x
00474.14 | [R] | Pump2Alarms2.ParameterVerificatonErrEEPROM |  | EEPROM error in parameter area (85) | 0 = No alarm 1 = Alarm |  | bool | x | x
00474.15 | [R] | Pump2Alarms2.DriveProtectMeasFault |  | Motor drive protection measurement fault (163) | 0 = No alarm 1 = Alarm |  | bool | x | x
00475.1 | [R] | Pump2.Alarms3.Distrib.Pumpmodulecomm.Fault |  | Fault in pump module communication (225) | 0 = No alarm 1 = Alarm |  | bool | x | x
00475.4 | [R] | Pump2.Alarms3.PTCSensorSignalFault |  | PTC sensor fault (181) | 0 = No alarm 1 = Alarm |  | bool | x | x
00475.9 | [R] | Pump2.Alarms3.SetupConflict |  | Conflict in setup parameters for current measurement (163) | 0 = No alarm 1 = Alarm |  | bool | x | x
00475.10 | [R] | Pump2.Alarms3.GeneralHardwareFault |  | General hardware fault (72) | 0 = No alarm 1 = Alarm |  | bool | x | x
00476.7 | [R] | Pump2Warnings1.MotorLowVoltage |  | Motor voltage low | 0 = No warning 1 = Warning |  | bool | x | x
00476.8 | [R] | Pump2Warnings1.MotorHighVoltage |  | Motor voltage high | 0 = No warning 1 = Warning |  | bool | x | x
00476.15 | [R] | Pump2Warnings1.LoadContinuesDespiteMotorRelayIsOff |  | Load continues, but motor relay is off | 0 = No warning 1 = Warning |  | bool | x | x
00477.7 | [R] | Pump2Warnings2.MotorMaxStartsPerHour |  | Motor max starts per hour limit exceeded (21) | 0 = No warning 1 = Warning |  | bool | x | x
00477.8 | [R] | Pump2Warnings2.MotoroperatingtimeserviceLimitExceeded |  | Motor service time exceeded (12) | 0 = No warning 1 = Warning |  | bool | x | x
00478.4 | [R] | Pump2.Warnings3.PTCSensorSignalFault |  | PTC sensor fault (181) | 0 = No warning 1 = Warning |  | bool | x | x
00481 | [R] | Pump2PowerHI |  | Power consumption, pump 2 |  | 1 | W | x | x
00482 | [R] | Pump2PowerLO | [5 empty] | x | x
00483 | [R] | Pump2EnergyHI |  | Energy consumption, pump 2 |  | 0.1 | kWh | x | x
00484 | [R] | Pump2EnergyLO | [5 empty] | x | x
00485 | [R] | Pump2CosPhi |  | Motor cosine phi, pump 2 (latched value) |  | 0.01 |  | x | x
SIMULATION [R/W]
00703 | [W] | Simulation.EventCode |  | Event Code to simulate |  |  | enum | x | x
00704 | [W] | Simulation.DeviceType |  | Device type to simulate (0=System, 6=Pump) |  |  | enum | x | x
00705 | [W] | Simulation.DeviceNumber |  | Device number to simulate (1=Pump#1, 2=Pump#2) |  |  | enum | x | x
00708 | [W] | Simulation.Activate |  | Activation of event simulation (use 0xAA) | 0 = Deactivate 1 = Activate |  | bool | x | x
00709 | [R] | Simulation.ActiveCode |  | The active simulation event code |  |  | enum | x | x
USER REGISTERS [R/W]
00751 | [R/W] | UserLabel1 | Saved in EEPROM |  |  |  | unscaled | x | x
00752 | [R/W] | UserLabel2 | Saved in EEPROM |  |  |  | unscaled | x | x
00753 | [R/W] | UserLabel3 | Saved in EEPROM |  |  |  | unscaled | x | x
00754-00799 | [R/W] | UserLabel4...UserLabel49 | Saved in EEPROM |  |  |  | unscaled | x | x
00800 | [R/W] | UserLabel50 | Saved in EEPROM |  |  |  | unscaled | x | x
CLOCK SCHEDULER [R/W]
05001 | [R/W] | SetMonBegin1Hour |  | Monday Begin 1 time |  | 1 | h |  | x
05002 | [R/W] | SetMonBegin1Min |  | Monday Begin 1 time |  | 1 | m |  | x
05003 | [R/W] | SetMonEnd1Hour |  | Monday End 1 time |  | 1 | h |  | x
05004 | [R/W] | SetMonEnd1Min |  | Monday End 1 time |  | 1 | m |  | x
05005 | [R/W] | SetMonBegin2Hour |  | Monday Begin 2 time |  | 1 | h |  | x
05006 | [R/W] | SetMonBegin2Min |  | Monday Begin 2 time |  | 1 | m |  | x
05007 | [R/W] | SetMonEnd2Hour |  | Monday End 2 time |  | 1 | h |  | x
05008 | [R/W] | SetMonEnd2Min |  | Monday End 2 time |  | 1 | m |  | x
05009 | [R/W] | SetMonBegin3Hour |  | Monday Begin 3 time |  | 1 | h |  | x
05010 | [R/W] | SetMonBegin3Min |  | Monday Begin 3 time |  | 1 | m |  | x
05011 | [R/W] | SetMonEnd3Hour |  | Monday End 3 time |  | 1 | h |  | x
05012 | [R/W] | SetMonEnd3Min |  | Monday End 3 time |  | 1 | m |  | x
05013 | [R/W] | SetMonBegin4Hour |  | Monday Begin 4 time |  | 1 | h |  | x
05014 | [R/W] | SetMonBegin4Min |  | Monday Begin 4 time |  | 1 | m |  | x
05015 | [R/W] | SetMonEnd4Hour |  | Monday End 4 time |  | 1 | h |  | x
05016 | [R/W] | SetMonEnd4Min |  | Monday End 4 time |  | 1 | m |  | x
05017 | [R/W] | SetMonBegin5Hour |  | Monday Begin 5 time |  | 1 | h |  | x
05018 | [R/W] | SetMonBegin5Min |  | Monday Begin 5 time |  | 1 | m |  | x
05019 | [R/W] | SetMonEnd5Hour |  | Monday End 5 time |  | 1 | h |  | x
05020 | [R/W] | SetMonEnd5Min |  | Monday End 5 time |  | 1 | m |  | x
05021 | [R/W] | SetTueBegin1Hour |  | Tuesday Begin 1 time |  | 1 | h |  | x
05022 | [R/W] | SetTueBegin1Min |  | Tuesday Begin 1 time |  | 1 | m |  | x
05023 | [R/W] | SetTueEnd1Hour |  | Tuesday End 1 time |  | 1 | h |  | x
05024 | [R/W] | SetTueEnd1Min |  | Tuesday End 1 time |  | 1 | m |  | x
05025 | [R/W] | SetTueBegin2Hour |  | Tuesday Begin 2 time |  | 1 | h |  | x
05026 | [R/W] | SetTueBegin2Min |  | Tuesday Begin 2 time |  | 1 | m |  | x
05027 | [R/W] | SetTueEnd2Hour |  | Tuesday End 2 time |  | 1 | h |  | x
05028 | [R/W] | SetTueEnd2Min |  | Tuesday End 2 time |  | 1 | m |  | x
05029 | [R/W] | SetTueBegin3Hour |  | Tuesday Begin 3 time |  | 1 | h |  | x
05030 | [R/W] | SetTueBegin3Min |  | Tuesday Begin 3 time |  | 1 | m |  | x
05031 | [R/W] | SetTueEnd3Hour |  | Tuesday End 3 time |  | 1 | h |  | x
05032 | [R/W] | SetTueEnd3Min |  | Tuesday End 3 time |  | 1 | m |  | x
05033 | [R/W] | SetTueBegin4Hour |  | Tuesday Begin 4 time |  | 1 | h |  | x
05034 | [R/W] | SetTueBegin4Min |  | Tuesday Begin 4 time |  | 1 | m |  | x
05035 | [R/W] | SetTueEnd4Hour |  | Tuesday End 4 time |  | 1 | h |  | x
05036 | [R/W] | SetTueEnd4Min |  | Tuesday End 4 time |  | 1 | m |  | x
05037 | [R/W] | SetTueBegin5Hour |  | Tuesday Begin 5 time |  | 1 | h |  | x
05038 | [R/W] | SetTueBegin5Min |  | Tuesday Begin 5 time |  | 1 | m |  | x
05039 | [R/W] | SetTueEnd5Hour |  | Tuesday End 5 time |  | 1 | h |  | x
05040 | [R/W] | SetTueEnd5Min |  | Tuesday End 5 time |  | 1 | m |  | x
05041 | [R/W] | SetWedBegin1Hour |  | Wednesday Begin 1 time |  | 1 | h |  | x
05042 | [R/W] | SetWedBegin1Min |  | Wednesday Begin 1 time |  | 1 | m |  | x
05043 | [R/W] | SetWedEnd1Hour |  | Wednesday End 1 time |  | 1 | h |  | x
05044 | [R/W] | SetWedEnd1Min |  | Wednesday End 1 time |  | 1 | m |  | x
05045 | [R/W] | SetWedBegin2Hour |  | Wednesday Begin 2 time |  | 1 | h |  | x
05046 | [R/W] | SetWedBegin2Min |  | Wednesday Begin 2 time |  | 1 | m |  | x
05047 | [R/W] | SetWedEnd2Hour |  | Wednesday End 2 time |  | 1 | h |  | x
05048 | [R/W] | SetWedEnd2Min |  | Wednesday End 2 time |  | 1 | m |  | x
05049 | [R/W] | SetWedBegin3Hour |  | Wednesday Begin 3 time |  | 1 | h |  | x
05050 | [R/W] | SetWedBegin3Min |  | Wednesday Begin 3 time |  | 1 | m |  | x
05051 | [R/W] | SetWedEnd3Hour |  | Wednesday End 3 time |  | 1 | h |  | x
05052 | [R/W] | SetWedEnd3Min |  | Wednesday End 3 time |  | 1 | m |  | x
05053 | [R/W] | SetWedBegin4Hour |  | Wednesday Begin 4 time |  | 1 | h |  | x
05054 | [R/W] | SetWedBegin4Min |  | Wednesday Begin 4 time |  | 1 | m |  | x
05055 | [R/W] | SetWedEnd4Hour |  | Wednesday End 4 time |  | 1 | h |  | x
05056 | [R/W] | SetWedEnd4Min |  | Wednesday End 4 time |  | 1 | m |  | x
05057 | [R/W] | SetWedBegin5Hour |  | Wednesday Begin 5 time |  | 1 | h |  | x
05058 | [R/W] | SetWedBegin5Min |  | Wednesday Begin 5 time |  | 1 | m |  | x
05059 | [R/W] | SetWedEnd5Hour |  | Wednesday End 5 time |  | 1 | h |  | x
05060 | [R/W] | SetWedEnd5Min |  | Wednesday End 5 time |  | 1 | m |  | x
05061 | [R/W] | SetThuBegin1Hour |  | Thursday Begin 1 time |  | 1 | h |  | x
05062 | [R/W] | SetThuBegin1Min |  | Thursday Begin 1 time |  | 1 | m |  | x
05063 | [R/W] | SetThuEnd1Hour |  | Thursday End 1 time |  | 1 | h |  | x
05064 | [R/W] | SetThuEnd1Min |  | Thursday End 1 time |  | 1 | m |  | x
05065 | [R/W] | SetThuBegin2Hour |  | Thursday Begin 2 time |  | 1 | h |  | x
05066 | [R/W] | SetThuBegin2Min |  | Thursday Begin 2 time |  | 1 | m |  | x
05067 | [R/W] | SetThuEnd2Hour |  | Thursday End 2 time |  | 1 | h |  | x
05068 | [R/W] | SetThuEnd2Min |  | Thursday End 2 time |  | 1 | m |  | x
05069 | [R/W] | SetThuBegin3Hour |  | Thursday Begin 3 time |  | 1 | h |  | x
05070 | [R/W] | SetThuBegin3Min |  | Thursday Begin 3 time |  | 1 | m |  | x
05071 | [R/W] | SetThuEnd3Hour |  | Thursday End 3 time |  | 1 | h |  | x
05072 | [R/W] | SetThuEnd3Min |  | Thursday End 3 time |  | 1 | m |  | x
05073 | [R/W] | SetThuBegin4Hour |  | Thursday Begin 4 time |  | 1 | h |  | x
05074 | [R/W] | SetThuBegin4Min |  | Thursday Begin 4 time |  | 1 | m |  | x
05075 | [R/W] | SetThuEnd4Hour |  | Thursday End 4 time |  | 1 | h |  | x
05076 | [R/W] | SetThuEnd4Min |  | Thursday End 4 time |  | 1 | m |  | x
05077 | [R/W] | SetThuBegin5Hour |  | Thursday Begin 5 time |  | 1 | h |  | x
05078 | [R/W] | SetThuBegin5Min |  | Thursday Begin 5 time |  | 1 | m |  | x
05079 | [R/W] | SetThuEnd5Hour |  | Thursday End 5 time |  | 1 | h |  | x
05080 | [R/W] | SetThuEnd5Min |  | Thursday End 5 time |  | 1 | m |  | x
05081 | [R/W] | SetFriBegin1Hour |  | Friday Begin 1 time |  | 1 | h |  | x
05082 | [R/W] | SetFriBegin1Min |  | Friday Begin 1 time |  | 1 | m |  | x
05083 | [R/W] | SetFriEnd1Hour |  | Friday End 1 time |  | 1 | h |  | x
05084 | [R/W] | SetFriEnd1Min |  | Friday End 1 time |  | 1 | m |  | x
05085 | [R/W] | SetFriBegin2Hour |  | Friday Begin 2 time |  | 1 | h |  | x
05086 | [R/W] | SetFriBegin2Min |  | Friday Begin 2 time |  | 1 | m |  | x
05087 | [R/W] | SetFriEnd2Hour |  | Friday End 2 time |  | 1 | h |  | x
05088 | [R/W] | SetFriEnd2Min |  | Friday End 2 time |  | 1 | m |  | x
05089 | [R/W] | SetFriBegin3Hour |  | Friday Begin 3 time |  | 1 | h |  | x
05090 | [R/W] | SetFriBegin3Min |  | Friday Begin 3 time |  | 1 | m |  | x
05091 | [R/W] | SetFriEnd3Hour |  | Friday End 3 time |  | 1 | h |  | x
05092 | [R/W] | SetFriEnd3Min |  | Friday End 3 time |  | 1 | m |  | x
05093 | [R/W] | SetFriBegin4Hour |  | Friday Begin 4 time |  | 1 | h |  | x
05094 | [R/W] | SetFriBegin4Min |  | Friday Begin 4 time |  | 1 | m |  | x
05095 | [R/W] | SetFriEnd4Hour |  | Friday End 4 time |  | 1 | h |  | x
05096 | [R/W] | SetFriEnd4Min |  | Friday End 4 time |  | 1 | m |  | x
05097 | [R/W] | SetFriBegin5Hour |  | Friday Begin 5 time |  | 1 | h |  | x
05098 | [R/W] | SetFriBegin5Min |  | Friday Begin 5 time |  | 1 | m |  | x
05099 | [R/W] | SetFriEnd5Hour |  | Friday End 5 time |  | 1 | h |  | x
05100 | [R/W] | SetFriEnd5Min |  | Friday End 5 time |  | 1 | m |  | x
05101 | [R/W] | SetSatBegin1Hour |  | Saturday Begin 1 time |  | 1 | h |  | x
05102 | [R/W] | SetSatBegin1Min |  | Saturday Begin 1 time |  | 1 | m |  | x
05103 | [R/W] | SetSatEnd1Hour |  | Saturday End 1 time |  | 1 | h |  | x
05104 | [R/W] | SetSatEnd1Min |  | Saturday End 1 time |  | 1 | m |  | x
05105 | [R/W] | SetSatBegin2Hour |  | Saturday Begin 2 time |  | 1 | h |  | x
05106 | [R/W] | SetSatBegin2Min |  | Staurday Begin 2 time |  | 1 | m |  | x
05107 | [R/W] | SetSatEnd2Hour |  | Saturday End 2 time |  | 1 | h |  | x
05108 | [R/W] | SetSatEnd2Min |  | Saturday End 2 time |  | 1 | m |  | x
05109 | [R/W] | SetSatBegin3Hour |  | Saturday Begin 3 time |  | 1 | h |  | x
05110 | [R/W] | SetSatBegin3Min |  | Saturday Begin 3 time |  | 1 | m |  | x
05111 | [R/W] | SetSatEnd3Hour |  | Saturday End 3 time |  | 1 | h |  | x
05112 | [R/W] | SetSatEnd3Min |  | Staurday End 3 time |  | 1 | m |  | x
05113 | [R/W] | SetSatBegin4Hour |  | Saturday Begin 4 time |  | 1 | h |  | x
05114 | [R/W] | SetSatBegin4Min |  | Saturday Begin 4 time |  | 1 | m |  | x
05115 | [R/W] | SetSatEnd4Hour |  | Saturday End 4 time |  | 1 | h |  | x
05116 | [R/W] | SetSatEnd4Min |  | Saturday End 4 time |  | 1 | m |  | x
05117 | [R/W] | SetSatBegin5Hour |  | Saturday Begin 5 time |  | 1 | h |  | x
05118 | [R/W] | SetSatBegin5Min |  | Saturday Begin 5 time |  | 1 | m |  | x
05119 | [R/W] | SetSatEnd5Hour |  | Saturday End 5 time |  | 1 | h |  | x
05120 | [R/W] | SetSatEnd5Min |  | Saturday End 5 time |  | 1 | m |  | x
05121 | [R/W] | SetSunBegin1Hour |  | Sunday Begin 1 time |  | 1 | h |  | x
05122 | [R/W] | SetSunBegin1Min |  | Sunday Begin 1 time |  | 1 | m |  | x
05123 | [R/W] | SetSunEnd1Hour |  | Sunday End 1 time |  | 1 | h |  | x
05124 | [R/W] | SetSunEnd1Min |  | Sunday End 1 time |  | 1 | m |  | x
05125 | [R/W] | SetSunBegin2Hour |  | Sunday Begin 2 time |  | 1 | h |  | x
05126 | [R/W] | SetSunBegin2Min |  | Sunday Begin 2 time |  | 1 | m |  | x
05127 | [R/W] | SetSunEnd2Hour |  | Sunday End 2 time |  | 1 | h |  | x
05128 | [R/W] | SetSunEnd2Min |  | Sunday End 2 time |  | 1 | m |  | x
05129 | [R/W] | SetSunBegin3Hour |  | Sunday Begin 3 time |  | 1 | h |  | x
05130 | [R/W] | SetSunBegin3Min |  | Sunday Begin 3 time |  | 1 | m |  | x
05131 | [R/W] | SetSunEnd3Hour |  | Sunday End 3 time |  | 1 | h |  | x
05132 | [R/W] | SetSunEnd3Min |  | Sunday End 3 time |  | 1 | m |  | x
05133 | [R/W] | SetSunBegin4Hour |  | Sunday Begin 4 time |  | 1 | h |  | x
05134 | [R/W] | SetSunBegin4Min |  | Sunday Begin 4 time |  | 1 | m |  | x
05135 | [R/W] | SetSunEnd4Hour |  | Sunday End 4 time |  | 1 | h |  | x
05136 | [R/W] | SetSunEnd4Min |  | Sunday End 4 time |  | 1 | m |  | x
05137 | [R/W] | SetSunBegin5Hour |  | Sunday Begin 5 time |  | 1 | h |  | x
05138 | [R/W] | SetSunBegin5Min |  | Sunday Begin 5 time |  | 1 | m |  | x
05139 | [R/W] | SetSunEnd5Hour |  | Sunday End 5 time |  | 1 | h |  | x
05140 | [R/W] | SetSunEnd5Min |  | Sunday End 5 time |  | 1 | m |  | x
EVENT LOG [R]
06001 | [R] | NoOfEventsInLog |  |  |  |  | unscaled | x | x
06002 | [R] | EventIDLog1 |  |  |  |  | unscaled | x | x
06003 | [R] | EventCodeLog1 |  |  |  |  | enum | x | x
06004 | [R] | EventSourceLog1 |  |  |  |  | enum | x | x
06005 | [R] | EventDeviceNo |  |  |  |  | unscaled | x | x
06006 | [R] | EventTypeAndConditionLog1 |  |  |  |  | enum | x | x
06007 | [R] | EventTimeStampLog1HI |  |  |  |  | 1 s | x | x
06008 | [R] | EventTimeStampLog1LO | [5 empty] | x | x
06009 | [R] | EventIDLog2 |  |  |  |  | unscaled | x | x
06010 | [R] | EventCodeLog2 |  |  |  |  | enum | x | x
06011 | [R] | EventSourceLog2 |  |  |  |  | enum | x | x
06012 | [R] | EventDeviceNo |  |  |  |  | unscaled | x | x
06013 | [R] | EventTypeAndConditionLog2 |  |  |  |  | enum | x | x
06014 | [R] | EventTimeStampLog2HI |  |  |  |  | 1 s | x | x
06015 | [R] | EventTimeStampLog2LO | [5 empty] | x | x
Continue list for event logs 3 - 39 | [7 empty] | x | x
06275 | [R] | EventIDLog40 |  |  |  |  | unscaled | x | x
06276 | [R] | EventCodeLog40 |  |  |  |  | enum | x | x
06277 | [R] | EventSourceLog40 |  |  |  |  | enum | x | x
06278 | [R] | EventDeviceNo |  |  |  |  | unscaled | x | x
06279 | [R] | EventTypeAndConditionLog40 |  |  |  |  | enum | x | x
06280 | [R] | EventTimeStampLog40HI |  |  |  |  | 1 s | x | x
06281 | [R] | EventTimeStampLog40LO | [5 empty] | x | x

## SQ
SoftCIM Modbus RTU SQ controller profile
Sheet version: |  | V01.00.08
Change date (d-m-y): |  | 2025-05-16
All addresses are registers (16 bit), and the address is written in decimal format
Reg. addr. | Access | Modbus parameter name | Description | Bool/Enum description | Modbus Scale | Modbus Unit | Modbus Offset
CIM CONFIG [R/W] - All saved in EEPROM
00003 | [R/W] | Config.SoftwareDefinedModbusAddress | Uset to configure the Modbus slave address [1; 247 ] from bus (Modbus RTU only). Saved in EEPROM |  |  | unscaled
00004 | [R/W] | Config.SoftwareDefinedBitRate | Uset to configure the Modbus bit rate from bus (Modbus RTU only). | 0 = 1200 1 = 2400 2 = 4800 3 = 9600 4 = 19200 5 = 38400 |  | enum
00005.0 | [R/W] | Config.AutoAckControlBits | Acknowlege behaviour of control bits Saved in EEPROM. 0 = Control bits are manually lowered. 1 = Control bits are automatically lowered, when module receives the event. (default) | 0 = Manual, 1 = Automatic |  | bool
00006.0 | [R/W] | Config.ReadWriteSeparation | Separate reads from writes Saved in EEPROM. 0 = Registers are overwritten with values (default) 1 = Register readback is put into seperate registers | 0 = No separation 1 = Separate registers |  | bool
00009 | [R/W] | Config.SoftwareDefinedParity | Used to configure the parity setting from bus (Modbus RTU only). Saved in EEPROM. | 0 = No parity 1 = Even parity 2 = Odd parity |  | enum
00010 | [R/W] | Config.SoftwareDefinedStopBit | Used to configure the stop bit setting from bus (Modbus RTU only). Saved in EEPROM. | 0 = Not defined 1 = 1 stop bit 2 = 2 stop bit |  | enum
00012 | [R/W] | Config.Watchdog | Used to configure the watchdog timeout [5; 3600]s. 0=Disable from bus. Saved in EEPROM. Default = 0 (Disabled). |  | 1 | s
CIM STATUS [R]
00023 | [R] | CIMSoftwareVersionNumber | Software version number (CIM module firmware version) |  |  | unscaled
00024 | [R] | ActualModbusAddress | Actual modbus slave address (Read only) |  |  | unscaled
00030 | [R] | Unit Family | Grundfos product family | 0 = - 1 = UPE/MAGNA pump 2 = MGE 7 = Motor Protection Unit 17 = Multi-E 21 = MPC / Multi-B 25 = CU 351 - CR Monitor 26 = CU 36x - Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller LC 241/242 48 = Level Controller LC 231 65 = SQ Controller CU 202/302 255 = N/A |  | enum
00031 | [R] | Unit Type | Grundfos product type |  |  | unscaled
00032 | [R] | Unit Version | Grundfos product version |  |  | unscaled
00034 | [R] | ProductSoftwareVersionHI | Product software version (BCD digit 1-4 aa.bb) |  |  | BCD number
00035 | [R] | ProductSoftwareVersionLO | Product software version (BCD digit 5-8 cc.dd) |  |  | BCD number
00036 | [R] | ProductSoftwareDayMonth | Product software date (BCD ddmm) |  |  | BCD number
00037 | [R] | ProductSoftwareYear | Product software date (BCD yyyy) |  |  | BCD number
CONTROL AND SETTINGS [W]
00101.0 | [W] | SystemControl.ResetAlarm | Reset Alarm,.Rising edge | 0 = No resetting 1 = Reset alarm |  | bool
00101.2 | [W] | SystemControl.ResetEventLog | Reset event log. Rising edge | 0 = No resetting 1 = Reset event log |  | bool
00101.10 | [W] | SystemControl.PumpOut | Pump all water out of the well. Rising edge | 0 = No command 1 = Pump Out command |  | bool
00103 | [W] | PumpControl | Manual control of pump. On value change | 0 = Auto 1 = Force Start 2 = Force Stop 255 = - |  | enum
00110 | [W] | SetEventLogClearID | Selects last record in event log record to clear. On value change |  |  | unscaled
00112 | [W] | SetRealTimeClockHI | Set Real Time Clock (32 bit UNIX format) high order. On value change |  | 1 | s
00113 | [W] | SetRealTimeClockLO | Set Real Time Clock (32 bit UNIX format) low order. This triggers the update On value change. |  |  | s
00114 | [W] | SetRtcSecond | Set Real Time Clock (Seconds) |  |  | enum
00115 | [W] | SetRtcMinute | Set Real Time Clock (Minutes) |  |  | enum
00116 | [W] | SetRtcHour | Set Real Time Clock (Hours) |  |  | enum
00117 | [W] | SetRtcDay | Set Real Time Clock (Day) |  |  | enum
00118 | [W] | SetRtcMonth | Set Real Time Clock (Month) |  |  | enum
00119 | [W] | SetRtcYear | Set Real Time Clock (Year - after 2000) |  |  | enum
00120.0 | [W] | SetRtc | Set Real Time Clock (Trigger of normal format) |  |  | bool
00122 | [W] | SetHighLevel | Set high level. On value change |  | 0.01 | m
00124 | [W] | SetDryRunningLevel | Set dry running level. On value change |  | 0.01 | m
00126 | [W] | SetStartLevelPump | Set start level pump. On value change |  | 0.01 | m
00127 | [W] | SetStopLevelPump | Set stop level pump. On value change |  | 0.01 | m
00185 | [W] | SetControlMode | Set the SQ Controller control mode. On value change | 0=Monitoring, CU 202/203 1=Filling, CU 202 On/Off level control 2=Emptying, CU 202 On/Off level control 3=Pressure Control, CU 202 On/Off pressure control 4=Constant Frequency, CU 302 speed controlled (NA) 5=Const. Pressure, CU 302 speed controlled pressure 6=Pump Out, CU 302/202 speed control / On/off control 7=Const. Temp., CU 302 speed controlled temp. (NA) 8=Constant Flow, CU 302 speed controlled flow (NA) 9=Constant Level, CU 302 speed controlled level (NA) |  | enum
00186 | [W] | SetSetpoint | Set the SQ Controller setpoint. Scaling according to Control mode enum. Triggered on value change. 0-3: Not applicable, setting the reference has not effect 4: Control Mode Constant Frequency: 0.01 % 5: Control Mode Constant Pressure: 0.001 bar 6: Control Mode Pump Out: 0.01 % 7: Control Mode Constant Temperature: 1 C 8: Control Mode Constant Flow: 0.1 m3/h 9: Control Mode Constant Level: 0.01 m >9: Not applicable, setting the reference has not effect |  |  | CtrMode dependent
STATUS [R]
00201.0 | [R] | Acknowledge.ResetAlarm | Acknowledge of Reset Alarm command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.1 | [R] | Acknowledge.SetRtc | Acknowledge of Set Real Time Clock command | 0 = No acknowledge 1 = Acknowledged |  | bool
00201.2 | [R] | Acknowledge.ResetEventLog | Acknowledge of Reset Event Log command | 0 = No acknowledge 1 = Acknowledged |  | bool
00202.1 | [R] | Status.Alarm | Presence of an alarm in LC controller | 0 = No Alarm 1 = Alarm present |  | bool
00202.2 | [R] | Status.Warning | Presence of a warning in LC controller | 0 = No warning 1 = Warning present |  | bool
00202.3 | [R] | Status.ManualControl | Manual or auto control | 0 = Auto control 1 = Manual control |  | bool
00210.1 | [R] | SystemAlarms1.HighLevel | High level (191) | 0 = No Alarm 1 = Alarm present |  | bool
00210.3 | [R] | SystemAlarms1.DryRunning | Dry running alarm (57) | 0 = No Alarm 1 = Alarm present |  | bool
00210.5 | [R] | SystemAlarms1.FloatSwitchSequenceInconsistency | Float switch sequence inconsistency (205) | 0 = No Alarm 1 = Alarm present |  | bool
00210.11 | [R] | SystemAlarms1.Distributed I/O module comm. Fault | I/O module communication alarm (226) | 0 = No Alarm 1 = Alarm present |  | bool
00211.0 | [R] | SystemAlarms2.Battery/UPS fault | Battery alarm (248) | 0 = No Alarm 1 = Alarm present |  | bool
00211.13 | [R] | SystemAlarms2.AI1SignalFault | AI sensor 1 signal fault (165) | 0 = No Alarm 1 = Alarm present |  | bool
00212.1 | [R] | SystemAlarms3.WaterOnFloor | Water on floor alarm (229) | 0 = No Alarm 1 = Alarm present |  | bool
00212.10 | [R] | SystemAlarms3.ExternalFaultSignal | External fault signal alarm (3) | 0 = No Alarm 1 = Alarm present |  | bool
00213.1 | [R] | SystemWarnings1.HighLevel | High level (191) | 0 = No warning 1 = Warning present |  | bool
00214.13 | [R] | SystemWarnings2.AI1SignalFault | AI sensor 1 signal fault (165) | 0 = No Alarm 1 = Alarm present |  | bool
00215.1 | [R] | SystemWarnings3.WaterOnFloor | Water on floor warning (229) | 0 = No warning 1 = Warning present |  | bool
00215.10 | [R] | SystemWarnings3.ExternalFaultSignal | External fault signal warning (3) | 0 = No warning 1 = Warning present |  | bool
00215.12 | [R] | SystemWarnings3.Intrusion | Intrusion (Door opened) (117) | 0 = No warning 1 = Warning present |  | bool
00216 | [R] | EventLogLatestID | Latest ID of event log |  |  | unscaled
00217 | [R] | NumberOfFloatSwitches | Amount of float switches in system |  |  | unscaled
00218.0 | [R] | FloatSwitchesStatus.Switch1 | Status of float switch 1 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00218.1 | [R] | FloatSwitchesStatus.Switch2 | Status of float switch 2 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00218.2 | [R] | FloatSwitchesStatus.Switch3 | Status of float switch 3 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00218.3 | [R] | FloatSwitchesStatus.Switch4 | Status of float switch 4 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00218.4 | [R] | FloatSwitchesStatus.Switch5 | Status of float switch 5 | 0 = Off (Float switch down) 1 = On (Float switch up) |  | bool
00219 | [R] | FloatSwitch1Function | Function of float switch 1 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum
00220 | [R] | FloatSwitch2Function | Function of float switch 2 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum
00221 | [R] | FloatSwitch3Function | Function of float switch 3 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum
00222 | [R] | FloatSwitch4Function | Function of float switch 4 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum
00223 | [R] | FloatSwitch5Function | Function of float switch 5 | 0 = Not used 1 = Dry running 3 = Stop all pumps 11 = Start/Stop 14 = Start 1 (1st pump) 15 = Start 2 (2nd pump) 23 = High level 255 = Not available 65535 = Not available |  | enum
00224.0 | [R] | Sensors.LevelControlSensor | Presence of level sensor for control | 0 = Sensor not present 1 = Sensor present |  | bool
00224.2 | [R] | Sensors.FloatSwithces | Presence of float switches for control | 0 = Float switches not present 1 = Float Switches present |  | bool
00224.3 | [R] | Sensors.FlowSensor | Presence of flow sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.4 | [R] | Sensors.Power/EnergySensor | Presence of power/energy sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.5 | [R] | Sensors.UserDefinedAIsensor1present | Presence of AI sensor 1 | 0 = Sensor not present 1 = Sensor present |  | bool
00224.6 | [R] | Sensors.UserDefinedAIsensor2present | Presence of AI sensor 2 | 0 = Sensor not present 1 = Sensor present |  | bool
00224.7 | [R] | Sensors.UserDefinedAIsensor3present | Presence of AI sensor 3 | 0 = Sensor not present 1 = Sensor present |  | bool
00224.8 | [R] | Sensors.UserDefinedAIsensor4present | Presence of AI sensor 4 | 0 = Sensor not present 1 = Sensor present |  | bool
00224.9 | [R] | Sensors.UserDefinedAIsensor5present | Presence of AI sensor 5 | 0 = Sensor not present 1 = Sensor present |  | bool
00224.10 | [R] | Sensors.TurbiditySensor | Presence of turbidity sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.11 | [R] | Sensors.PHSensor | Presence of PH sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.12 | [R] | Sensors.ConductivitySensor | Presence of conductivity sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.13 | [R] | Sensors.PulseFlowMeter | Presence of pulse flow meter | 0 = Flow meter not present 1 = Flow meter present |  | bool
00224.14 | [R] | Sensors.PressureSensor | Presence of pressure sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00224.15 | [R] | Sensors.LevelSensor | Presence of level sensor | 0 = Sensor not present 1 = Sensor present |  | bool
00228 | [R] | UNIXRealTimeClockHI | Real Time Clock (32 bit UNIX format) |  | 1 | s
00229 | [R] | UNIXRealTimeClockLO
00230 | [R] | RtcSecond | Real Time Clock (Seconds) |  |  | enum
00231 | [R] | RtcMinute | Real Time Clock (Minutes) |  |  | enum
00232 | [R] | RtcHour | Real Time Clock (Hours) |  |  | enum
00233 | [R] | RtcDay | Real Time Clock (Day) |  |  | enum
00234 | [R] | RtcMonth | Real Time Clock (Month) |  |  | enum
00235 | [R] | RtcYear | Real Time Clock (Year) |  |  | enum
00241 | [R] | HighLevel | Actual high level |  | 0.01 | m
00243 | [R] | DryRunningLevel | Actual dry running level |  | 0.01 | m
00245 | [R] | StartLevelPump | Actual start level of pump |  | 0.01 | m
00246 | [R] | StopLevelPump | Actual stop level of pump |  | 0.01 | m
00272.5 | [R] | SystemAlarms5.LevelSettingsInvalid | Start or stop level setting invalid or missing (25.1009) | 0 = No Alarm 1 = Alarm present |  | bool
00272.6 | [R] | SystemAlarms5.Missing AnalogLevelSetting | Analog level sensor not configured (25.1010) | 0 = No Alarm 1 = Alarm present |  | bool
00272.7 | [R] | SystemAlarms5.DublicateSwitchSetting | Dublicateswitch setting (25.1011) | 0 = No Alarm 1 = Alarm present |  | bool
00272.8 | [R] | SystemAlarms5.OperatingOnBatteryBackup | Operating on battery backup (142) | 0 = No Alarm 1 = Alarm present |  | bool
00272.9 | [R] | SystemAlarms5.TempProtectionConfiguredButDisabled | PT motor temp. protection meas configured but disabled (25.1020) | 0 = No Alarm 1 = Alarm present |  | bool
00273.1 | [R] | SystemWarnings5.ExternalWarningSignal | External warning signal (46) | 0 = No warning 1 = Warning present |  | bool
00273.3 | [R] | SystemWarnings5.RealTimeClockOutOfOrder | Real time clock out of order warning (157) | 0 = No warning 1 = Warning present |  | bool
00273.5 | [R] | SystemWarnings5.LevelSettingsInvalid | Start or stop level setting invalid or missing (25.1009) | 0 = No warning 1 = Warning present |  | bool
00273.6 | [R] | SystemWarnings5.Missing AnalogLevelSetting | Analog level sensor not configured (25.1010) | 0 = No warning 1 = Warning present |  | bool
00273.7 | [R] | SystemWarnings5.DublicateSwitchSetting | Dublicateswitch setting (25.1011) | 0 = No warning 1 = Warning present |  | bool
00273.8 | [R] | SystemWarning5.OperatingOnBatteryBackup | Operating on battery backup (142) | 0 = No warning 1 = Warning present |  | bool |  | x
00273.9 | [R] | SystemWarnings5.TempProtectConfiguredButDisabled | PT motor temp. protection meas configured but disabled (25.1020) | 0 = No warning 1 = Warning present |  | bool
00274 | [R] | AnalogIn1Min | AI1 sensor range minimum |  |  | unit
00275 | [R] | AnalogIn1Max | AI1 sensor range maximum |  |  | unit
00276 | [R] | AnalogIn1Unit | AI1 sensor unit |  |  | enum
00277 | [R] | AnalogIn2Min | AI2 sensor range minimum |  |  | unit
00278 | [R] | AnalogIn2Max | AI2 sensor range maximum |  |  | unit
00279 | [R] | AnalogIn2Unit | AI2 sensor unit |  |  | enum
00280 | [R] | AnalogIn3Min | AI3 sensor range minimum (Not supported yet) |  |  | unit
00281 | [R] | AnalogIn3Max | AI3 sensor range maximum (Not supported yet) |  |  | unit
00282 | [R] | AnalogIn3Unit | AI3 sensor unit (Not supported yet) |  |  | enum
00283 | [R] | AnalogIn4Min | AI4 sensor range minimum (Not supported yet) |  |  | unit
00284 | [R] | AnalogIn4Max | AI4 sensor range maximum (Not supported yet) |  |  | unit
00285 | [R] | AnalogIn4Unit | AI4 sensor unit (Not supported yet) |  |  | enum
00286 | [R] | AnalogIn5Min | AI5 sensor range minimum (Not supported yet) |  |  | unit
00287 | [R] | AnalogIn5Max | AI5 sensor range maximum (Not supported yet) |  |  | unit
00288 | [R] | AnalogIn5Unit | AI5 sensor unit (Not supported yet) |  |  | enum
00289 | [R] | ActualControlMode | Actual Control Mode | 0=Monitoring, CU 202/203 1=Filling, CU 202 On/Off level control 2=Emptying, CU 202 On/Off level control 3=Pressure Control, CU 202 On/Off pressure control 4=Constant Frequency, CU 302 speed controlled 5=Const. Pressure, CU 302 speed controlled pressure 6=Pump Out, CU 302/202 speed control / On/off control 7=Const. Temp., CU 302 speed controlled temp. 8=Constant Flow, CU 302 speed controlled flow 9=Constant Level, CU 302 speed controlled level |  | enum
00290.0 | [R] | SystemAlarms6.SetupConflict.IllegalSensorOrSwitch | Setup Conflict. Illegal sensor/switch conf (25. 1001) | 0 = No Alarm 1 = Alarm present |  | bool
00290.1 | [R] | SystemAlarms6.SetupConflict.LevelCtrSettingsConflict | Setup Conflict. Level control settings conflict (25. 1005) | 0 = No Alarm 1 = Alarm present |  | bool
00290.2 | [R] | SystemAlarms6.SetupConflict.Control/ApplicationMode | Setup Conflict. Control mode incompatible with application (25.1014) | 0 = No Alarm 1 = Alarm present |  | bool
00290.3 | [R] | SystemAlarms6.NoFlow | No flow. Flow switch shows no flow (59) | 0 = No Alarm 1 = Alarm present |  | bool
00290.4 | [R] | SystemAlarms6.BatteryLow | Battery low (28) | 0 = No Alarm 1 = Alarm present |  | bool
00290.5 | [R] | SystemAlarms6.Limit1Exceeded | Limit 1 exceeded (133.1001) | 0 = No Alarm 1 = Alarm present |  | bool
00290.6 | [R] | SystemAlarms6.Limit2Exceeded | Limit 2 exceeded (133.1002) | 0 = No Alarm 1 = Alarm present |  | bool
00290.7 | [R] | SystemAlarms6.PumpingTimeExceeded | Pump Out did not finish within the set Pumping Time (200.1001) | 0 = No Alarm 1 = Alarm present |  | bool
00290.8 | [R] | SystemAlarms6.PressureBuildUpTimeExceeded | Pressure build-up within set time failed (200.1002) | 0 = No Alarm 1 = Alarm present |  | bool
00290.9 | [R] | SystemAlarms6.WaterLeakage | Water leakage detected (207) | 0 = No Alarm 1 = Alarm present |  | bool
00290.10 | [R] | SystemAlarms6.LowInputPower | Low input power, solar (60) | 0 = No Alarm 1 = Alarm present |  | bool
00290.11 | [R] | SystemAlarms6.Overpressure | Overpressure (210) | 0 = No Alarm 1 = Alarm present |  | bool
00290.12 | [R] | SystemAlarms6.Underpressure | Underpressure, could not pressurize system within time (211) | 0 = No Alarm 1 = Alarm present |  | bool
00290.13 | [R] | SystemAlarms6.SetuoConflict.PressureSettingTooLow | Pressure setting is below low-pressure alarm/stop level (25.1022) | 0 = No Alarm 1 = Alarm present |  | bool
00291.14 | [R] | SystemAlarms6.SetupConflict.ConfSensorConflictsWithAttachedSensor | Setup conflict. Conf sensor conflicts with attached sensor (25.1004) | 0 = No Alarm 1 = Alarm present |  | bool
00291.0 | [R] | SystemWarnings6.SetupConflict.IllegalSensorOrSwitch | Setup Conflict. Illegal sensor/switch conf (25. 1001) | 0 = No Warning 1 = Warning present |  | bool
00291.1 | [R] | SystemWarnings6.SetupConflict.LevelCtrSettingsConflict | Setup Conflict. Level control settings conflict (25. 1005) | 0 = No Warning 1 = Warning present |  | bool
00291.2 | [R] | SystemWarnings6.SetupConflict.Control/ApplicationMode | Setup Conflict. Control mode incompatible with application (25.1014) | 0 = No Warning 1 = Warning present |  | bool
00291.3 | [R] | SystemWarnings6.NoFlow | No flow. Flow switch shows no flow (59) | 0 = No Warning 1 = Warning present |  | bool
00291.4 | [R] | SystemWarnings6.BatteryLow | Battery low (28) | 0 = No Warning 1 = Warning present |  | bool
00291.5 | [R] | SystemWarnings6.Limit1Exceeded | Limit 1 exceeded (133.1001) | 0 = No Warning 1 = Warning present |  | bool
00291.6 | [R] | SystemWarnings6.Limit2Exceeded | Limit 2 exceeded (133.1002) | 0 = No Warning 1 = Warning present |  | bool
00291.7 | [R] | SystemWarnings6.PumpingTimeExceeded | Pump Out did not finish within the set Pumping Time (200.1001) | 0 = No Warning 1 = Warning present |  | bool
00291.8 | [R] | SystemWarnings6.PressureBuildUpTimeExceeded | Pressure build up within set time failed (200.1002) | 0 = No Warning 1 = Warning present |  | bool
00291.9 | [R] | SystemWarnings6.WaterLeakage | Water leakage detected (207) | 0 = No Warning 1 = Warning present |  | bool
00291.10 | [R] | SystemWarnings6.LowInputPower | Low input power, solar (60) | 0 = No Warning 1 = Warning present |  | bool
00291.11 | [R] | SystemWarnings6.Overpressure | Overpressure (210) | 0 = No Warning 1 = Warning present |  | bool
00291.12 | [R] | SystemWarnings6.Underpressure | Underpressure, could not pressurize system within time (211) | 0 = No Warning 1 = Warning present |  | bool
00291.13 | [R] | SystemWarnings6.SetuoConflict.PressureSettingTooLow | Pressure setting is below low-pressure alarm/stop level (25.1022) | 0 = No Warning 1 = Warning present |  | bool
00291.14 | [R] | SystemWarnings6.SetupConflict.ConfSensorConflictsWithAttachedSensor | Setup conflict. Conf sensor conflicts with attached sensor (25.1004) | 0 = No Warning 1 = Warning present |  | bool
SYSTEM DATA [R]
00301 | [R] | SystemWaterLevel | System water level |  | 0.01 | m
00308 | [R] | SystemPowerHI | System power consumption |  | 1 | W
00309 | [R] | SystemPowerLO
00310 | [R] | SystemEnergyHI | System energy consumption |  | 0.1 | kWh
00311 | [R] | SystemEnergyLO
00312 | [R] | SystemEnergyYesterday | System energy comsumption yesterday |  | 0.1 | kWh
00313 | [R] | SystemEnergyToday | System energy comsumption today |  | 0.1 | kWh
00329 | [R] | SystemOperatingTimeHI | System operating time |  | 1 | min
00330 | [R] | SystemOperatingTimeLO
00351 | [R] | UserAnalogInput1 | User analog input 1 |  | 0.1 | %
00352 | [R] | UserAnalogInput2 | User analog input 2 |  | 0.1 | %
00353 | [R] | UserAnalogInput3 | User analog input 3 |  | 0.1 | %
00378 | [R] | ActualSetpoint | Actual setpoint for SQ pump |  |  | CtrMode dependent
00379 | [R] | SensorFeedback | Feedback from controol loop sensor |  |  | CtrMode dependent
00380 | [R] | Pressure | Pressure |  | 0.001 | bar
00381 | [R] | Temperature | Temperature |  | 1 | C
00382 | [R] | UserAnalogOutput1 | User analog output AO1 |  | 0.1 | %
00383 | [R] | UserAnalogOutput2 | User analog output AO2 |  | 0.1 | %
00391 | [R] | UserDigitalInBlock1 | User digital inputs 15-0 |  |  | unscaled
00392 | [R] | UserDigitalInBlock2 | User digital inputs 31-16 |  |  | unscaled
00393 | [R] | UserDigitalOutput | User digital outputs |  |  | unscaled
00394 | [R] | UserAnalogInput4 | User analog input 4 |  | 0.1 | %
00395 | [R] | UserAnalogInput5 | User analog input 5 |  | 0.1 | %
PUMP [R]
00401.0 | [R] | PumpStatus.Presence | Presence of pump | 0 = No present 1 = Present |  | bool
00401.1 | [R] | PumpStatus.Running | Rotation status of pump | 0 = No rotation 1 = Rotation |  | bool
00401.3 | [R] | PumpStatus.Warning | Warning status of pump | 0 = No warning 1 = Warning |  | bool
00401.4 | [R] | PumpStatus.Alarm | Alarm status of pump | 0 = No alarm 1 = Alarm |  | bool
00402 | [R] | PumpControlSource | Control source of pump | 0 = Auto 1 = Manual by switch 2 = Manual by display 3 = Manual from bus 255 = - |  | enum
00403 | [R] | PumpConnectionType | Connection type of pump | 0 = Pump connected to wall mounted controller or not present 1 = Pump connected via pump module 255 = - |  | enum
00404 | [R] | PumpOprTimeHI | Operating time of pump |  | 1 | min
00405 | [R] | PumpOprTimeLO
00406 | [R] | PumpTimeToServiceHI | Time to service for pump |  | 1 | min
00407 | [R] | PumpTimeToServiceLO |  |  |  | min
00408 | [R] | PumpOprTimeYesterday | Operating time yesterday, pump |  | 1 | min
00409 | [R] | PumpOprTimeToday | Operating time today, pump |  | 1 | min
00410 | [R] | PumpLatestOprTime | Latest operating time for pump |  | 1 | s
00411 | [R] | PumpStartCounterHI | Start counter for pump |  |  | unscaled
00412 | [R] | PumpStartCounterLO |  |  |  | unscaled
00413 | [R] | PumpStartCounterYesterday | Start counter yesterday, pump |  |  | unscaled
00414 | [R] | PumpStartCounterToday | Start counter today, pump |  |  | unscaled
00415 | [R] | PumpStartsPerHour | Number of starts within the latest hour, pump |  |  | unscaled
00418 | [R] | PumpCurrent | Motor current, pump |  | 0.1 | A
00419 | [R] | PumpLatestCurrent | Latest motor current, pump |  | 0.1 | A
00420 | [R] | PumpVoltage | Motor voltage, pump |  | 0.1 | V
00423.7 | [R] | PumpAlarms1.MotorLowVoltage | Motor voltage low (40) | 0 = No alarm 1 = Alarm |  | bool
00423.8 | [R] | PumpAlarms1.MotorHighVoltage | Motor voltage high (32) | 0 = No alarm 1 = Alarm |  | bool
00423.10 | [R] | PumpAlarms1.MotorOverload | Motor overload (48) | 0 = No alarm 1 = Alarm |  | bool
00424.8 | [R] | PumpAlarms2.MotoroperatingtimeserviceLimitExceeded | Motor service time exceeded (12) | 0 = No alarm 1 = Alarm |  | bool
00425.8 | [R] | PumpAlarms3.PumpComm.Fault | Pump communication fault (10) | 0 = No alarm 1 = Alarm |  | bool
00426.7 | [R] | PumpWarnings1.MotorLowVoltage | Motor voltage low (40) | 0 = No warning 1 = Warning |  | bool
00426.8 | [R] | PumpWarnings1.MotorHighVoltage | Motor voltage high (32) | 0 = No warning 1 = Warning |  | bool
00426.10 | [R] | PumpWarnings1.MotorOverload | Motor overload (48) | 0 = No warning 1 = Warning |  | bool
00427.8 | [R] | PumpWarnings2.MotoroperatingtimeserviceLimitExceeded | Motor service time exceeded (12) | 0 = No warning 1 = Warning |  | bool
00428.8 | [R] | Pump.Warnings3.PumpCommFault | Pump communication fault (10) | 0 = No warning 1 = Warning |  | bool
00431 | [R] | PumpPowerHI | Power consumption, pump |  | 1 | W
00432 | [R] | PumpPowerLO
00433 | [R] | PumpEnergyHI | Energy consumption, pump |  | 0.1 | kWh
00434 | [R] | PumpEnergyLO
00435 | [R] | PumpCosPhi | Motor cosine phi, pump (latched value) |  | 0.01
00436 | [R] | PumpSpeed | Speed, pump |  | 1 | rpm
00437 | [R] | PumpMotorTemp | Motor temperature, pump |  | 1 | C
00441.10 | [R] | PumpAlarms4.DryRunning | Dry running (57) | 0 = No alarm 1 = Alarm |  | bool
00441.13 | [R] | PumpAlarms4.PumpBlocked | Pump blocked alarm (51) | 0 = No alarm 1 = Alarm |  | bool
00442.10 | [R] | PumpWarnings4.DryRunning | Dry running (57) | 0 = No warning 1 = Warning |  | bool
00442.13 | [R] | PumpWarnings4.PumpBlocked | Pump blocked warning (51) | 0 = No alarm 1 = Warning |  | bool
00451.0 | [R] | PumpAlarms5.OverVoltage.InrushCircuitDetection | Overvoltage detected by inrush circuit (32.1001) | 0 = No alarm 1 = Alarm |  | bool
00451.1 | [R] | PumpAlarms5.OverVoltage.HardwareShutdown | Overvoltage, hardware shutdown, DPFC (32.1002) | 0 = No alarm 1 = Alarm |  | bool
00451.2 | [R] | PumpAlarms5.OverVoltage.DCLinkVoltage | Overvoltage, DC link voltage too high (32.1003) | 0 = No alarm 1 = Alarm |  | bool
00451.3 | [R] | PumpAlarms5.BlockedMotor.Rotor/StatorLostSyncInClLoop | Blocked motor, rotor/stator out of sync. In closed loop opr. (51.1001) | 0 = No alarm 1 = Alarm |  | bool
00451.4 | [R] | PumpAlarms5.BlockedMotor.Rotor/StatorLostSyncStarting | Blocked motor, rotor/stator out of sync. during start (51.1002) | 0 = No alarm 1 = Alarm |  | bool
00451.5 | [R] | PumpAlarms5.BlockedMotor.DeratingDownToMin | Blocked motor, running min speed due to derating function (51.1003) | 0 = No alarm 1 = Alarm |  | bool
00451.6 | [R] | PumpAlarms5.DryRunningDetectedDueToPowerMeas | Dry running detection based on pump power measurement (57.1002) | 0 = No alarm 1 = Alarm |  | bool
00451.7 | [R] | PumpAlarms5.DryRunningDetectedByLevelMeas | Dry running detection based on level measurement (57.1003) | 0 = No alarm 1 = Alarm |  | bool
00451.8 | [R] | PumpAlarms5.DryRunningDetectedByInletPress | Dry running detection based on inlet press. measurement (57.1004) | 0 = No alarm 1 = Alarm |  | bool
00451.9 | [R] | PumpAlarms5.DryRunningDetectedByDedicatedSignal | Dry running detection based on dedicated dry run signal (57.1005) | 0 = No alarm 1 = Alarm |  | bool
00451.10 | [R] | PumpAlarms5.DryRunningDetectedBySensorInPump | Dry running detection with dry run sensor integrated in pump (57.1006) | 0 = No alarm 1 = Alarm |  | bool
00451.11 | [R] | PumpAlarms5.OvertemperatureInFreqConvModule | Overtemperature, internal frequency converter module (67) | 0 = No alarm 1 = Alarm |  | bool
00452.0 | [R] | PumpWarnings5.OverVoltage.InrushCircuitDetection | Overvoltage detected by inrush circuit (32.1001) | 0 = No warning 1 = Warning |  | bool
00452.1 | [R] | PumpWarnings5.OverVoltage.HardwareShutdown | Overvoltage, hardware shutdown, DPFC (32.1002) | 0 = No warning 1 = Warning |  | bool
00452.2 | [R] | PumpWarnings5.OverVoltage.DCLinkVoltage | Overvoltage, DC link voltage too high (32.1003) | 0 = No warning 1 = Warning |  | bool
00452.3 | [R] | PumpWarnings5.BlockedMotor.Rotor/StatorLostSyncInClLoop | Blocked motor, rotor/stator out of sync. In closed loop opr. (51.1001) | 0 = No warning 1 = Warning |  | bool
00452.4 | [R] | PumpWarnings5.BlockedMotor.Rotor/StatorLostSyncStarting | Blocked motor, rotor/stator out of sync. During start (51.1002) | 0 = No warning 1 = Warning |  | bool
00452.5 | [R] | PumpWarnings5.BlockedMotor.DeratingDownToMin | Blocked motor, running min speed due to derating function (51.1003) | 0 = No warning 1 = Warning |  | bool
00452.6 | [R] | PumpWarnings5.DryRunningDetectedDueToPowerMeas | Dry running detection based on pump power measurement (57.1002) | 0 = No warning 1 = Warning |  | bool
00452.7 | [R] | PumpWarnings5.DryRunningDetectedByLevelMeas | Dry running detection based on level measurement (57.1003) | 0 = No warning 1 = Warning |  | bool
00452.8 | [R] | PumpWarnings5.DryRunningDetectedByInletPress | Dry running detection based on inlet press. measurement (57.1004) | 0 = No warning 1 = Warning |  | bool
00452.9 | [R] | PumpWarnings5.DryRunningDetectedByDedicatedSignal | Dry running detection based on dedicated dry run signal (57.1005) | 0 = No warning 1 = Warning |  | bool
00452.10 | [R] | PumpWarnings5.DryRunningDetectedBySensorInPump | Dry running detection with dry run sensor integrated in pump (57.1006) | 0 = No warning 1 = Warning |  | bool
00452.11 | [R] | PumpWarnings5.OvertemperatureInFreqConvModule | Overtemperature, internal frequency converter module (67) | 0 = No warning 1 = Warning |  | bool
00453.0 | [R] | PumpAlarms6.HardwareShutDown | Hardware shutdown (73) | 0 = No alarm 1 = Alarm |  | bool
00453.1 | [R] | PumpAlarms6.HardwareShutDown.DCLinkCurrentHighStopping | Hardware shutdown, DC link current too high during stopping (73.1001) | 0 = No alarm 1 = Alarm |  | bool
00453.2 | [R] | PumpAlarms6.HardwareShutDown.ADCMuxTestFailed | Hardware shutdown, A/D converter MUX test failed (73.1002) | 0 = No alarm 1 = Alarm |  | bool
00453.3 | [R] | PumpAlarms6.HardwareShutDown.DCLinkCurrentHighClLoop | Hardware shutdown, DC link current too high in cl. operation (73.1003) | 0 = No alarm 1 = Alarm |  | bool
00453.4 | [R] | PumpAlarms6.HardwareShutDown.CurrentMeasFault | Hardware shutdown, fault in motor current measurement (73.1004) | 0 = No alarm 1 = Alarm |  | bool
00453.5 | [R] | PumpAlarms6.HardwareShutDown.NotBreakedBeforeStart | Hardware shutdown, impossible to brake motor before start (73.1005) | 0 = No alarm 1 = Alarm |  | bool
00454.0 | [R] | PumpWarnings6.HardwareShutDown | Hardware shutdown (73) | 0 = No warning 1 = Warning |  | bool
00454.1 | [R] | PumpWarnings6.HardwareShutDown.DCLinkCurrentHighStopping | Hardware shutdown, DC link current too high during stopping (73.1001) | 0 = No warning 1 = Warning |  | bool
00454.2 | [R] | PumpWarnings6.HardwareShutDown.ADCMuxTestFailed | Hardware shutdown, A/D converter MUX test failed (73.1002) | 0 = No warning 1 = Warning |  | bool
00454.3 | [R] | PumpWarnings6.HardwareShutDown.DCLinkCurrentHighClLoop | Hardware shutdown, DC link current too high in cl. operation (73.1003) | 0 = No warning 1 = Warning |  | bool
00454.4 | [R] | PumpWarnings6.HardwareShutDown.CurrentMeasFault | Hardware shutdown, fault in motor current measurement (73.1004) | 0 = No warning 1 = Warning |  | bool
00454.5 | [R] | PumpWarnings6.HardwareShutDown.NotBreakedBeforeStart | Hardware shutdown, impossible to brake motor beore start (73.1005) | 0 = No warning 1 = Warning |  | bool
SIMULATION [R/W]
00703 | [W] | Simulation.EventCode | Event Code to simulate |  |  | enum
00704 | [W] | Simulation.DeviceType | Device type to simulate (0=System, 6=Pump) |  |  | enum
00705 | [W] | Simulation.DeviceNumber | Device number to simulate (1=Pump#1, 2=Pump#2) |  |  | enum
00708 | [W] | Simulation.Activate | Activation of event simulation (use 0xAA) | 0 = Deactivate 1 = Activate |  | bool
00709 | [R] | Simulation.ActiveCode | The active simulation event code |  |  | enum
USER REGISTERS [R/W]
00751 | [R/W] | UserLabel1 | Saved in EEPROM |  |  | unscaled
00752 | [R/W] | UserLabel2 | Saved in EEPROM |  |  | unscaled
00753 | [R/W] | UserLabel3 | Saved in EEPROM |  |  | unscaled
00754-00799 | [R/W] | UserLabel4...UserLabel49 | Saved in EEPROM |  |  | unscaled
00800 | [R/W] | UserLabel50 | Saved in EEPROM |  |  | unscaled
CLOCK SCHEDULER [R/W]
05001 | [R/W] | SetMonBegin1Hour | Monday Begin 1 time |  | 1 | h
05002 | [R/W] | SetMonBegin1Min | Monday Begin 1 time |  | 1 | m
05003 | [R/W] | SetMonEnd1Hour | Monday End 1 time |  | 1 | h
05004 | [R/W] | SetMonEnd1Min | Monday End 1 time |  | 1 | m
05005 | [R/W] | SetMonBegin2Hour | Monday Begin 2 time |  | 1 | h
05006 | [R/W] | SetMonBegin2Min | Monday Begin 2 time |  | 1 | m
05007 | [R/W] | SetMonEnd2Hour | Monday End 2 time |  | 1 | h
05008 | [R/W] | SetMonEnd2Min | Monday End 2 time |  | 1 | m
05009 | [R/W] | SetMonBegin3Hour | Monday Begin 3 time |  | 1 | h
05010 | [R/W] | SetMonBegin3Min | Monday Begin 3 time |  | 1 | m
05011 | [R/W] | SetMonEnd3Hour | Monday End 3 time |  | 1 | h
05012 | [R/W] | SetMonEnd3Min | Monday End 3 time |  | 1 | m
05013 | [R/W] | SetMonBegin4Hour | Monday Begin 4 time |  | 1 | h
05014 | [R/W] | SetMonBegin4Min | Monday Begin 4 time |  | 1 | m
05015 | [R/W] | SetMonEnd4Hour | Monday End 4 time |  | 1 | h
05016 | [R/W] | SetMonEnd4Min | Monday End 4 time |  | 1 | m
05017 | [R/W] | SetMonBegin5Hour | Monday Begin 5 time |  | 1 | h
05018 | [R/W] | SetMonBegin5Min | Monday Begin 5 time |  | 1 | m
05019 | [R/W] | SetMonEnd5Hour | Monday End 5 time |  | 1 | h
05020 | [R/W] | SetMonEnd5Min | Monday End 5 time |  | 1 | m
05021 | [R/W] | SetTueBegin1Hour | Tuesday Begin 1 time |  | 1 | h
05022 | [R/W] | SetTueBegin1Min | Tuesday Begin 1 time |  | 1 | m
05023 | [R/W] | SetTueEnd1Hour | Tuesday End 1 time |  | 1 | h
05024 | [R/W] | SetTueEnd1Min | Tuesday End 1 time |  | 1 | m
05025 | [R/W] | SetTueBegin2Hour | Tuesday Begin 2 time |  | 1 | h
05026 | [R/W] | SetTueBegin2Min | Tuesday Begin 2 time |  | 1 | m
05027 | [R/W] | SetTueEnd2Hour | Tuesday End 2 time |  | 1 | h
05028 | [R/W] | SetTueEnd2Min | Tuesday End 2 time |  | 1 | m
05029 | [R/W] | SetTueBegin3Hour | Tuesday Begin 3 time |  | 1 | h
05030 | [R/W] | SetTueBegin3Min | Tuesday Begin 3 time |  | 1 | m
05031 | [R/W] | SetTueEnd3Hour | Tuesday End 3 time |  | 1 | h
05032 | [R/W] | SetTueEnd3Min | Tuesday End 3 time |  | 1 | m
05033 | [R/W] | SetTueBegin4Hour | Tuesday Begin 4 time |  | 1 | h
05034 | [R/W] | SetTueBegin4Min | Tuesday Begin 4 time |  | 1 | m
05035 | [R/W] | SetTueEnd4Hour | Tuesday End 4 time |  | 1 | h
05036 | [R/W] | SetTueEnd4Min | Tuesday End 4 time |  | 1 | m
05037 | [R/W] | SetTueBegin5Hour | Tuesday Begin 5 time |  | 1 | h
05038 | [R/W] | SetTueBegin5Min | Tuesday Begin 5 time |  | 1 | m
05039 | [R/W] | SetTueEnd5Hour | Tuesday End 5 time |  | 1 | h
05040 | [R/W] | SetTueEnd5Min | Tuesday End 5 time |  | 1 | m
05041 | [R/W] | SetWedBegin1Hour | Wednesday Begin 1 time |  | 1 | h
05042 | [R/W] | SetWedBegin1Min | Wednesday Begin 1 time |  | 1 | m
05043 | [R/W] | SetWedEnd1Hour | Wednesday End 1 time |  | 1 | h
05044 | [R/W] | SetWedEnd1Min | Wednesday End 1 time |  | 1 | m
05045 | [R/W] | SetWedBegin2Hour | Wednesday Begin 2 time |  | 1 | h
05046 | [R/W] | SetWedBegin2Min | Wednesday Begin 2 time |  | 1 | m
05047 | [R/W] | SetWedEnd2Hour | Wednesday End 2 time |  | 1 | h
05048 | [R/W] | SetWedEnd2Min | Wednesday End 2 time |  | 1 | m
05049 | [R/W] | SetWedBegin3Hour | Wednesday Begin 3 time |  | 1 | h
05050 | [R/W] | SetWedBegin3Min | Wednesday Begin 3 time |  | 1 | m
05051 | [R/W] | SetWedEnd3Hour | Wednesday End 3 time |  | 1 | h
05052 | [R/W] | SetWedEnd3Min | Wednesday End 3 time |  | 1 | m
05053 | [R/W] | SetWedBegin4Hour | Wednesday Begin 4 time |  | 1 | h
05054 | [R/W] | SetWedBegin4Min | Wednesday Begin 4 time |  | 1 | m
05055 | [R/W] | SetWedEnd4Hour | Wednesday End 4 time |  | 1 | h
05056 | [R/W] | SetWedEnd4Min | Wednesday End 4 time |  | 1 | m
05057 | [R/W] | SetWedBegin5Hour | Wednesday Begin 5 time |  | 1 | h
05058 | [R/W] | SetWedBegin5Min | Wednesday Begin 5 time |  | 1 | m
05059 | [R/W] | SetWedEnd5Hour | Wednesday End 5 time |  | 1 | h
05060 | [R/W] | SetWedEnd5Min | Wednesday End 5 time |  | 1 | m
05061 | [R/W] | SetThuBegin1Hour | Thursday Begin 1 time |  | 1 | h
05062 | [R/W] | SetThuBegin1Min | Thursday Begin 1 time |  | 1 | m
05063 | [R/W] | SetThuEnd1Hour | Thursday End 1 time |  | 1 | h
05064 | [R/W] | SetThuEnd1Min | Thursday End 1 time |  | 1 | m
05065 | [R/W] | SetThuBegin2Hour | Thursday Begin 2 time |  | 1 | h
05066 | [R/W] | SetThuBegin2Min | Thursday Begin 2 time |  | 1 | m
05067 | [R/W] | SetThuEnd2Hour | Thursday End 2 time |  | 1 | h
05068 | [R/W] | SetThuEnd2Min | Thursday End 2 time |  | 1 | m
05069 | [R/W] | SetThuBegin3Hour | Thursday Begin 3 time |  | 1 | h
05070 | [R/W] | SetThuBegin3Min | Thursday Begin 3 time |  | 1 | m
05071 | [R/W] | SetThuEnd3Hour | Thursday End 3 time |  | 1 | h
05072 | [R/W] | SetThuEnd3Min | Thursday End 3 time |  | 1 | m
05073 | [R/W] | SetThuBegin4Hour | Thursday Begin 4 time |  | 1 | h
05074 | [R/W] | SetThuBegin4Min | Thursday Begin 4 time |  | 1 | m
05075 | [R/W] | SetThuEnd4Hour | Thursday End 4 time |  | 1 | h
05076 | [R/W] | SetThuEnd4Min | Thursday End 4 time |  | 1 | m
05077 | [R/W] | SetThuBegin5Hour | Thursday Begin 5 time |  | 1 | h
05078 | [R/W] | SetThuBegin5Min | Thursday Begin 5 time |  | 1 | m
05079 | [R/W] | SetThuEnd5Hour | Thursday End 5 time |  | 1 | h
05080 | [R/W] | SetThuEnd5Min | Thursday End 5 time |  | 1 | m
05081 | [R/W] | SetFriBegin1Hour | Friday Begin 1 time |  | 1 | h
05082 | [R/W] | SetFriBegin1Min | Friday Begin 1 time |  | 1 | m
05083 | [R/W] | SetFriEnd1Hour | Friday End 1 time |  | 1 | h
05084 | [R/W] | SetFriEnd1Min | Friday End 1 time |  | 1 | m
05085 | [R/W] | SetFriBegin2Hour | Friday Begin 2 time |  | 1 | h
05086 | [R/W] | SetFriBegin2Min | Friday Begin 2 time |  | 1 | m
05087 | [R/W] | SetFriEnd2Hour | Friday End 2 time |  | 1 | h
05088 | [R/W] | SetFriEnd2Min | Friday End 2 time |  | 1 | m
05089 | [R/W] | SetFriBegin3Hour | Friday Begin 3 time |  | 1 | h
05090 | [R/W] | SetFriBegin3Min | Friday Begin 3 time |  | 1 | m
05091 | [R/W] | SetFriEnd3Hour | Friday End 3 time |  | 1 | h
05092 | [R/W] | SetFriEnd3Min | Friday End 3 time |  | 1 | m
05093 | [R/W] | SetFriBegin4Hour | Friday Begin 4 time |  | 1 | h
05094 | [R/W] | SetFriBegin4Min | Friday Begin 4 time |  | 1 | m
05095 | [R/W] | SetFriEnd4Hour | Friday End 4 time |  | 1 | h
05096 | [R/W] | SetFriEnd4Min | Friday End 4 time |  | 1 | m
05097 | [R/W] | SetFriBegin5Hour | Friday Begin 5 time |  | 1 | h
05098 | [R/W] | SetFriBegin5Min | Friday Begin 5 time |  | 1 | m
05099 | [R/W] | SetFriEnd5Hour | Friday End 5 time |  | 1 | h
05100 | [R/W] | SetFriEnd5Min | Friday End 5 time |  | 1 | m
05101 | [R/W] | SetSatBegin1Hour | Saturday Begin 1 time |  | 1 | h
05102 | [R/W] | SetSatBegin1Min | Saturday Begin 1 time |  | 1 | m
05103 | [R/W] | SetSatEnd1Hour | Saturday End 1 time |  | 1 | h
05104 | [R/W] | SetSatEnd1Min | Saturday End 1 time |  | 1 | m
05105 | [R/W] | SetSatBegin2Hour | Saturday Begin 2 time |  | 1 | h
05106 | [R/W] | SetSatBegin2Min | Staurday Begin 2 time |  | 1 | m
05107 | [R/W] | SetSatEnd2Hour | Saturday End 2 time |  | 1 | h
05108 | [R/W] | SetSatEnd2Min | Saturday End 2 time |  | 1 | m
05109 | [R/W] | SetSatBegin3Hour | Saturday Begin 3 time |  | 1 | h
05110 | [R/W] | SetSatBegin3Min | Saturday Begin 3 time |  | 1 | m
05111 | [R/W] | SetSatEnd3Hour | Saturday End 3 time |  | 1 | h
05112 | [R/W] | SetSatEnd3Min | Staurday End 3 time |  | 1 | m
05113 | [R/W] | SetSatBegin4Hour | Saturday Begin 4 time |  | 1 | h
05114 | [R/W] | SetSatBegin4Min | Saturday Begin 4 time |  | 1 | m
05115 | [R/W] | SetSatEnd4Hour | Saturday End 4 time |  | 1 | h
05116 | [R/W] | SetSatEnd4Min | Saturday End 4 time |  | 1 | m
05117 | [R/W] | SetSatBegin5Hour | Saturday Begin 5 time |  | 1 | h
05118 | [R/W] | SetSatBegin5Min | Saturday Begin 5 time |  | 1 | m
05119 | [R/W] | SetSatEnd5Hour | Saturday End 5 time |  | 1 | h
05120 | [R/W] | SetSatEnd5Min | Saturday End 5 time |  | 1 | m
05121 | [R/W] | SetSunBegin1Hour | Sunday Begin 1 time |  | 1 | h
05122 | [R/W] | SetSunBegin1Min | Sunday Begin 1 time |  | 1 | m
05123 | [R/W] | SetSunEnd1Hour | Sunday End 1 time |  | 1 | h
05124 | [R/W] | SetSunEnd1Min | Sunday End 1 time |  | 1 | m
05125 | [R/W] | SetSunBegin2Hour | Sunday Begin 2 time |  | 1 | h
05126 | [R/W] | SetSunBegin2Min | Sunday Begin 2 time |  | 1 | m
05127 | [R/W] | SetSunEnd2Hour | Sunday End 2 time |  | 1 | h
05128 | [R/W] | SetSunEnd2Min | Sunday End 2 time |  | 1 | m
05129 | [R/W] | SetSunBegin3Hour | Sunday Begin 3 time |  | 1 | h
05130 | [R/W] | SetSunBegin3Min | Sunday Begin 3 time |  | 1 | m
05131 | [R/W] | SetSunEnd3Hour | Sunday End 3 time |  | 1 | h
05132 | [R/W] | SetSunEnd3Min | Sunday End 3 time |  | 1 | m
05133 | [R/W] | SetSunBegin4Hour | Sunday Begin 4 time |  | 1 | h
05134 | [R/W] | SetSunBegin4Min | Sunday Begin 4 time |  | 1 | m
05135 | [R/W] | SetSunEnd4Hour | Sunday End 4 time |  | 1 | h
05136 | [R/W] | SetSunEnd4Min | Sunday End 4 time |  | 1 | m
05137 | [R/W] | SetSunBegin5Hour | Sunday Begin 5 time |  | 1 | h
05138 | [R/W] | SetSunBegin5Min | Sunday Begin 5 time |  | 1 | m
05139 | [R/W] | SetSunEnd5Hour | Sunday End 5 time |  | 1 | h
05140 | [R/W] | SetSunEnd5Min | Sunday End 5 time |  | 1 | m
EVENT LOG [R]
06001 | [R] | NoOfEventsInLog |  |  |  | unscaled
06002 | [R] | EventIDLog1 |  |  |  | unscaled
06003 | [R] | EventCodeLog1 |  |  |  | enum
06004 | [R] | EventSourceLog1 |  |  |  | enum
06005 | [R] | EventDeviceNo |  |  |  | unscaled
06006 | [R] | EventTypeAndConditionLog1 |  |  |  | enum
06007 | [R] | EventTimeStampLog1HI |  |  |  | 1 s
06008 | [R] | EventTimeStampLog1LO
06009 | [R] | EventIDLog2 |  |  |  | unscaled
06010 | [R] | EventCodeLog2 |  |  |  | enum
06011 | [R] | EventSourceLog2 |  |  |  | enum
06012 | [R] | EventDeviceNo |  |  |  | unscaled
06013 | [R] | EventTypeAndConditionLog2 |  |  |  | enum
06014 | [R] | EventTimeStampLog2HI |  |  |  | 1 s
06015 | [R] | EventTimeStampLog2LO
Continue list for event logs 3 - 39
06275 | [R] | EventIDLog40 |  |  |  | unscaled
06276 | [R] | EventCodeLog40 |  |  |  | enum
06277 | [R] | EventSourceLog40 |  |  |  | enum
06278 | [R] | EventDeviceNo |  |  |  | unscaled
06279 | [R] | EventTypeAndConditionLog40 |  |  |  | enum
06280 | [R] | EventTimeStampLog40HI |  |  |  | 1 s
06281 | [R] | EventTimeStampLog40LO

## DDA
GRUNDFOS CIM 200/500 and SoftCIM MODBUS PROFILE FOR DDA |  |  |  |  | GENI comm. Error(reg, values) | 217 | 159
All addresses are registers (16 bit), and the address is written in decimal format.
Sheet version: V01.02.04
Change date (d-m-y): 15-10-2018
Reg. addr. | Access | Modbus parameter name | Modbus notes - development | Description | Bool/Enum description | Modbus Scale | Modbus Unit
DEVICE CONFIG [R/W] - All saved in EEPROM
00001 | [R/W] | Config.SlaveMinimumReplyDelay | Saved in EEPROM | For adding a reply delay in ms (used with radio modem) |  | 1 | ms
00002 | [R/W] | RESERVED
00003 | [R/W] | Config.SoftwareDefinedModbusAddress | Saved in EEPROM. If switch value is invalid, then use the value in this register as Modbus address. Make 0xE7 the default value. | Set a Modbus slave address to use if the address switches are set to an invalid value (Modbus RTU only). |  |  | unscaled
00004 | [R/W] | Config.ModbusBitRate | 0 = 1200 [def.], 1 = 2400 2 = 4800, 3 = 9600, 4 = 19200, 5 = 38400 Saved in EEPROM | If set to software defined, use this bit rate (Modbus RTU only). | 0 = 1200 1 = 2400 2 = 4800 3 = 9600 4 = 19200 5 = 38400 |  | enum
00005 | [R/W] | Config.AutoAckControlBits | Saved in EEPROM. 0 = Controls bits are manually lowered. 1 = Control bits are automatically lowered, when module receives the event. (default) | Acknowlege behaviour of control bits | 0 = Manual, 1 = Automatic |  | bool
00006 |  | RESERVED
00007 | [R/W] | Config.ScadaCallbackRegister | Register in the master used for unsolicited messages. CIM 250 SW handles EEPROM. | Register in the master used for unsolicited messages. (GSM/GRPS only) |  |  | unscaled
00008 | [R/W] | Config.NoDataActivityTimeout | The elapsed time with no data activity before the module issues a "GPRS restart". CIM 250 SW handles EEPROM. | The elapsed time with no data activity before the module issues a "GPRS restart". (GSM/GRPS only) |  | 1 | min
00009 | [R/W] | Config.SoftwareDefinedParity | Saved in EEPROM. Default value = 0. | If software defined, use this parity setting (Modbus RTU only). | 0 = No parity 1 = Even parity 2 = Odd parity |  | enum
00010 | [R/W] | Config.SoftwareDefinedStopBit | Saved in EEPROM. Default value = 1. | If software defined, use this stop bit setting (Modbus RTU only). | 0 = Not defined 1 = 1 stop bit 2 = 2 stop bit |  | enum
00011 | [R/W] | Config.ScadaPinCode | Code to use if ScadaPinCode is enabled. | Code to use if ScadaPinCode is enabled (GSM/GPRS only)
00013 | [R/W] | Config.GENIbusDiodeOff |  | Switching off the GENIbus diode (LED2) | 0=On (default) 1=Off |  | bool
DEVICE STATUS [R]
00021 | [R] | GENIbusCRCErrorCnt | GENIbus CRC err. | CRC error counter on GENIbus |  |  | unscaled
00022 | [R] | GENIbusDataErrorCnt | GENIbus Data err. | Data error counter on GENIbus |  |  | unscaled
00023 | [R] | VersionNumber | Shows version number | Software version number (Must be read as raw hexadecimal) |  |  | unscaled
00024 | [R] | ActualModbusAddress | Shows actual address | Actual modbus slave address (Read only) |  |  | unscaled
00025 | [R] | GENIbusTXcount HI | GENIbus TX telegram count | Transmit counter on GENIbus |  |  | unscaled
00026 | [R] | GENIbusTXcount LO
00027 | [R] | GENIbusRXcount HI | GENIbus RX telegram count | Receive counter on GENIbus |  |  | unscaled
00028 | [R] | GENIbusRXcount LO
00029.0 | [R] | ScadaPinCodeEnabled |  | Determines if the use of a Scada Pin Code is enabled (GSM/GPRS only) | 0 = Pin code disabled 1 = Pin code enabled
00029.1 | [R] | WriteAccessStatus |  | Determines if write (control) access is granted or not (GSM/GPRS only) | 0 = No write access 1 = Write access
00030 | [R] | GrundfosUnitFamily | Grundfos specific | Grundfos product family | 0 = - 1 = UPE/MAGNA pump 2 = MGE 7 = Motor Protection Unit 17 = Multi-E 21 = MPC / Multi-B 25 = CU 351 - CR Monitor 26 = CU 361 - Dedicated Controls 28 = CIU, SEG AutoAdapt 30 = Smart digital dosing pump 38 = MAGNA3 multi-pump 39 = Multi-E model H/I 46 = SP Controller CU 2X1 255 = N/A |  | enum
00031 | [R] | GrundfosUnitType | Grundfos specific | Grundfos product type number |  |  | unscaled
00032 | [R] | GrundfosUnitVersion | Grundfos specific | Grundfos product version number |  |  | unscaled
00033 | [R] | BatteryState | Equal to gsm_battery_state (5, 52) | State of cellular battery | 0 = Battery not present 1 = Battery must be replaced 2 = Battery charging 3 = Battery needs charging, but temperature too high 4 = Battery needs charging, but temperature too low 5 = Battery Low 6 = Battery OK 255 = Battery state not available |  | enum
GSM REAL TIME CLOCK [R/W] (ONLY AVAILABLE IN CIM 25X!)
00080 | [W] | SetUNIXRealTimeClockHI | On value change | Set Real Time Clock (32 bit UNIX format) (GSM/GPRS only) |  | 1 | s
00081 | [W] | SetUNIXRealTimeClockLO | On value change
00082 | [W] | SetRtcSecond | On value change | Set Real Time Clock (Seconds) (GSM/GPRS only) |  |  | enum
00083 | [W] | SetRtcMinute | On value change | Set Real Time Clock (Minutes) (GSM/GPRS only) |  |  | enum
00084 | [W] | SetRtcHour | On value change | Set Real Time Clock (Hours) (GSM/GPRS only) |  |  | enum
00085 | [W] | SetRtcDay | On value change | Set Real Time Clock (Day) (GSM/GPRS only) |  |  | enum
00086 | [W] | SetRtcMonth | On value change | Set Real Time Clock (Month) (GSM/GPRS only) |  |  | enum
00087 | [W] | SetRtcYear | On value change | Set Real Time Clock (Year - after 2000) (GSM/GPRS only) |  |  | enum
00088.0 | [W] | SetRtc | Rising edge | Set Real Time Clock (Normal format) (GSM/GPRS only) | 0 = No command 1 = Set the clock |  | bool
00089 | [R] | Status.UNIXRealTimeClockHI |  | Real Time Clock (32 bit UNIX format) (GSM/GPRS only) |  | 1 | s
00090 | [R] | Status.UNIXRealTimeClockLO
00091 | [R] | Status.RtcSecond |  | Real time clock - Seconds (GSM/GPRS only) |  |  | enum
00092 | [R] | Status.RtcMinute |  | Real time clock - Minutes (GSM/GPRS only) |  |  | enum
00093 | [R] | Status.RtcHour |  | Real time clock - Hours (GSM/GPRS only) |  |  | enum
00094 | [R] | Status.RtcDay |  | Real time clock - Day of month (GSM/GPRS only) |  |  | enum
00095 | [R] | Status.RtcMonth |  | Real time clock - Month (GSM/GPRS only) |  |  | enum
00096 | [R] | Status.RtcYear |  | Real time clock - Year (after 2000) (GSM/GPRS only) |  |  | enum
00097.0 | [R] | Status.AcknowledgeSetRTC | 1 = Acknowledged | Acknowledge of Set Real Time Clock command (GSM/GPRS only) | 0 = No acknowledge 1 = Acknowledged |  | bool
CONTROL [W]
00101.0 | [W] | ModeSettings.RemoteAccessReq | 0 = Local, all outputs are not written to Common GENI. 1 = Remote | Set to Remote for bus control | 0 = Local 1 = Remote |  | bool
00101.1 | [W] | ModeSettings.Deaerating | 0 = Off 1 = On |  | 0 = Off 1 = On |  | bool
00101.2 | [W] | ModeSettings.AnalogueMode | 0 = 0-20mA 1 = 4-20mA | Type of analog signal (Must be in Analog Mode) | 0 = 0-20mA 1 = 4-20mA |  | bool
00101.3 | [W] | ModeSettings.TimerMode | 0 = Cycle timer 1 = Week timer | Type of Timer (Must be selected before entering Timer Mode) | 0 = Cycle timer 1 = Week timer |  | bool
00101.4 | [W] | ModeSettings.SlowModeActivate | 0 = Disable 1 = Enable | Suction stroke is slower (Snail icon in display) | 0 = Disable 1 = Enable |  | bool
00101.5 | [W] | ModeSettings.Velocity | 0 = Middle (50% velocity) 1 = High (25% velocity) | Slow Mode suction stroke velocity (Must be in Slow Mode) | 0 = Middle (50% velocity) 1 = High (25% velocity) |  | bool
00102.0 | [W] | Functions.AutoDeaeratingEnable | 0 = Disable 1 = Enable | Pump automatically deaerated at regular intervals (buble icon in display) | 0 = Disable 1 = Enable |  | bool
00102.1 | [W] | Functions.FlowControlEnable | 0 = Disable 1 = Enable | Flow control activation (Eye icon in display) | 0 = Disable 1 = Enable |  | bool
00102.2 | [W] | Functions.ModbusWatchdogEnable | 0 = Disable 1 = Enable |  | 0 = Disable 1 = Enable |  | bool
00102.3 | [W] | Functions.AutoFlowAdaptEnable | 0 = Disable 1 = Enable | Detects changes in parameters and adapts flow control (Flow Control must be enabled) | 0 = Disable 1 = Enable |  | bool
00102.4 | [W] | Functions.PulseMemoryEnable | 0 = Disable 1 = Enable | Memorizing of un-processed pulses | 0 = Disable 1 = Enable |  | bool
00103.0 | [W] | Commands.ResetFault | Event triggered | Reset fault | 0 = No action 1 = Reset fault |  | bool
00103.1 | [W] | Commands.Pulse | Event triggered | Send a single pulse | 0 = No action 1 = Pulse |  | bool
00103.2 | [W] | Commands.ResetVolumeCounter | Event triggered | Reset the volume counter | 0 = No action 1 = Reset counter |  | bool
00103.3 | [W] | Commands.SetRTC | Event triggered | Set real time clock | 0 = No action 1 = Set time |  | bool
00104 | [W] | ReqStartStop | 0 = Requested Start 1 = Requested Stop | Start/Stop control | 0 = Requested Start 1 = Requested Stop |  | enum
00105 | [W] | OperatingMode | 0 = Manual 1 = Pulse 2 = Analogue 3 = Timer 4 = Batch | Set the dosing Operating mode | 0 = Manual 1 = Pulse 2 = Analogue 3 = Timer 4 = Batch |  | enum
00106 | [W] | SetpointManualHI |  | Manual setpoint |  | 0.1 | ml/h
00107 |  | SetpointManualLO
00108 | [W] | SetPulseVolumeHI |  |  |  | 1 | nl
00109 |  | SetPulseVolumeLO
00110 | [W] | SetBatchDosingVolumeHI |  |  |  | 0.001 | ml
00111 |  | SetBatchDosingVolumeLO
00112 | [W] | SetBatchDosingTimeHI |  |  |  | 0.1 | s
00113 |  | SetBatchDosingTimeLO
00114 | [W] | SetPressureMax |  | Set Flow monitor max pressure (alarm limit), cannot be set lower than a pump dependant minumum value |  | 0.1 | bar
00115.0 | [W] | SetOutputRelay1 | 0 = Inactive 1 = Active | Control relay 1 | 0 = Inactive 1 = Active |  | bool
00115.1 | [W] | SetOutputRelay2 | 0 = Inactive 1 = Active | Control relay 2 | 0 = Inactive 1 = Active |  | bool
00116 | [W] | SetAnalogOutput | Data range: 0-20 mA |  |  | 0.001 | mA
00117 | [W] | SetDateTime.Year | From year 2000 | Select year (from year 2000) |  |  | enum
00118 | [W] | SetDateTime.Month | [1-12] | Select month [1-12] |  |  | enum
00119 | [W] | SetDateTime.Day | [1-31] | Select day [1-31] |  |  | enum
00120 | [W] | SetDateTime.Hour | [0-23] | Select hour [0-23] |  |  | enum
00121 | [W] | SetDateTime.Minute | [0-59] | Select minute [0-59] |  |  | enum
00122 | [W] | SetDateTime.Second | [0-59] | Select second [0-59] |  |  | enum
STATUS [R]
00201.0 | [R] | ActRemoteAccess | 0 = Local 1 = Remote |  | 0 = Local 1 = Remote |  | bool
00201.1 | [R] | ActDeaerating | 0 = Off 1 = On |  | 0 = Off 1 = On |  | bool
00201.2 | [R] | ActAnalogueMode | 0 = 0-20mA 1 = 4-20mA |  | 0 = 0-20mA 1 = 4-20mA |  | bool
00201.3 | [R] | ActTimerMode | 0 = Cycle timer 1 = Week timer |  | 0 = Cycle timer 1 = Week timer |  | bool
00201.4 | [R] | ActSlowMode | 0 = Inactive 1 = Active |  | 0 = Inactive 1 = Active |  | bool
00201.5 | [R] | ActVelocity | 0 = Middle (50% velocity) 1 = High (25% velocity) |  | 0 = Middle (50% velocity) 1 = High (25% velocity) |  | bool
00202.0 | [R] | AutoDeaeratingEnabled | 0 = Disabled 1 = Enabled |  | 0 = Disabled 1 = Enabled |  | bool
00202.1 | [R] | FlowControlEnabled | 0 = Disabled 1 = Enabled |  | 0 = Disabled 1 = Enabled |  | bool
00202.2 | [R] | ModbusWatchdogEnabled | 0 = Disabled 1 = Enabled |  | 0 = Disabled 1 = Enabled |  | bool
00202.3 | [R] | AutoFlowAdaptEnabled | 0 = Disabled 1 = Enabled |  | 0 = Disabled 1 = Enabled |  | bool
00202.4 | [R] | PulseMemoryEnabled | 0 = Disabled 1 = Enabled |  | 0 = Disabled 1 = Enabled |  | bool
00203.0 | [R] | ResetFaultAck |  | Acknowledge of Commands.ResetFault (103.0) | 0 = No ack 1 = Acknowledged |  | bool
00203.1 | [R] | PulseAck |  | Acknowledge of Commands.Pulse (103.1) | 0 = No ack 1 = Acknowledged |  | bool
00203.2 | [R] | ResetVolumeCounterAck |  | Acknowledge of Commands.RestVolumeCounter (103.2) | 0 = No ack 1 = Acknowledged |  | bool
00203.3 | [R] | SetRTCAck |  | Acknowledge of Commands.SetRTC (103.3) | 0 = No ack 1 = Acknowledged |  | bool
00204.0 | [R] | Dosing | 0 = No dosing (not running) 1 = Dosing (running) |  | 0 = No dosing 1 = Dosing |  | bool
00204.1 | [R] | Warning | 0 = No warning present 1 = Warning present |  | 0 = No warning present 1 = Warning present |  | bool
00204.2 | [R] | Fault | 0 = No fault present 1 = Fault present |  | 0 = No fault present 1 = Fault present |  | bool
00204.3 | [R] | BusControlLocallyEnabled | 0 = Profibus control disabled 1 = Profibus control enabled |  | 0 = Profibus control disabled 1 = Profibus control enabled |  | bool
00205 | [R] | ActualStartStop | 0 = Started 1 = Stopped 2 = Calibrating 3 = Service |  | 0 = Started 1 = Stopped 2 = Calibrating 3 = Service 255 = N/A |  | enum
00206 | [R] | ActualOperatingMode | 0 = Manual 1 = Pulse 2 = Analogue 3 = Timer 4 = Batch |  | 0 = Manual 1 = Pulse 2 = Analogue 3 = Timer 4 = Batch 255 = N/A |  | enum
00207 | [R] | ActualSetpointManualHI |  |  |  | 0.1 | ml/h
00208 | [R] | ActualSetpointManualLO
00209 | [R] | ActualPulseVolumeHI |  |  |  | 1 | nl
00210 | [R] | ActualPulseVolumeLO
00211 | [R] | ActualBatchDosingVolumeHI |  |  |  | 0.001 | ml
00212 | [R] | ActualBatchDosingVolumeLO
00213 | [R] | ActualBatchDosingTimeHI |  |  |  | 0.1 | s
00214 | [R] | ActualBatchDosingTimeLO
00215 | [R] | ActualPressureMax |  | Actual flow monitor max pressure (alarm limit) |  | 0.1 | bar
00216.0 | [R] | ControlSourceStates.StopFromHMI |  |  | 0 = Inactive 1 = Active |  | bool
00216.1 | [R] | ControlSourceStates.StopFromExternal |  |  | 0 = Inactive 1 = Active |  | bool
00216.2 | [R] | ControlSourceStates.StopFromBus |  |  | 0 = Inactive 1 = Active |  | bool
00217 | [R] | FaultCode |  | A Grundfos specific alarm code |  |  | enum
00218 | [R] | WarningCode |  | A Grundfos specific warning code |  |  | enum
00219.0 | [R] | WarningBits.BackPressureLow |  | Back pressure too low (Code 211) | 0 = Inactive 1 = Active |  | bool
00219.1 | [R] | WarningBits.GasInPumpHead |  | Gas in pump head (Code 35) | 0 = Inactive 1 = Active |  | bool
00219.2 | [R] | WarningBits.Cavitation |  | Cavitation (Code 208) | 0 = Inactive 1 = Active |  | bool
00219.3 | [R] | WarningBits.DischargeValveLeakage |  | Discharge valve leakage (Code 36) | 0 = Inactive 1 = Active |  | bool
00219.4 | [R] | WarningBits.SuctionValveLeakage |  | Suction valve leakage (Code 37) | 0 = Inactive 1 = Active |  | bool
00219.5 | [R] | WarningBits.VentingValveDefect |  | Venting valve defect (Code 38) | 0 = Inactive 1 = Active |  | bool
00219.6 | [R] | WarningBits.ServiceNow |  | Service now (Code 12) | 0 = Inactive 1 = Active |  | bool
00219.7 | [R] | WarningBits.ServiceSoon |  | Service soon (Code 33) | 0 = Inactive 1 = Active |  | bool
00219.8 | [R] | WarningBits.LowLevelInTank |  | Low level in tank (Code 206) | 0 = Inactive 1 = Active |  | bool
00219.9 | [R] | WarningBits.PowerFailure |  | Power failure (Code 6) | 0 = Inactive 1 = Active |  | bool
00219.10 | [R] | WarningBits.FlowControlCableDefect |  | Flow control cable defect (Code 169) | 0 = Inactive 1 = Active |  | bool
00219.11 | [R] | WarningBits.BatteryLow |  | Battery low (Code 28) | 0 = Inactive 1 = Active |  | bool
00219.12 | [R] | WarningBits.AveragePressureTooLow |  | Average pressure too low (Code 211) | 0 = Inactive 1 = Active |  | bool
00219.13 | [R] | WarningBits.PumpingCapacityTooLow |  | PumpingCapacity too low (Code 17) | 0 = Inactive 1 = Active |  | bool
00220 | [R] | Status.Year | From year 2000 |  |  |  | enum
00221 | [R] | Status.Month | [1-12] |  |  |  | enum
00222 | [R] | Status.Day | [1-31] |  |  |  | enum
00223 | [R] | Status.Hour | [0-23] |  |  |  | enum
00224 | [R] | Status.Minute | [0-59] |  |  |  | enum
00225 | [R] | Status.Second | [0-59] |  |  |  | enum
SYSTEM DATA [R]
00301 | [R] | DosingPressureMax |  | Maximum possible pressure in dosing head |  | 0.1 | bar
00302 | [R] | DosingCapacityMaxHI |  | Maximum possible flow |  | 0.1 | ml/h
00303 | [R] | DosingCapacityMaxLO
00304 | [R] | DosingCapacityReferenceHI |  | Dosing capacity setpoint shown in the pump display. Will show 0 if pump is stopped |  | 0.1 | ml/h
00305 | [R] | DosingCapacityReferenceLO
00306 | [R] | MeasuredDosingCapacityHI |  |  |  | 0.1 | ml/h
00307 | [R] | MeasuredDosingCapacityLO
00308 | [R] | MeasuredPressure |  | Measured absolute pressure. FlowControl must be enabled. |  | 0.1 | bar
00309 | [R] | PulseInputFrequency |  |  |  | 1 | /min
00310 | [R] | RemainingDosingVolumeHI |  | Actual remaining volume to be dosed. Used in "Batch" mode. |  | 0.001 | ml
00311 | [R] | RemainingDosingVolumeLO
00312 | [R] | VolumeTotalHI |  |  |  | 0.001 | l
00313 | [R] | VolumeTotalLO
00314 | [R] | VolumeTripCounterHI |  |  |  | 0.001 | l
00315 | [R] | VolumeTripCounterLO
00316 | [R] | AnalogInput |  |  |  | 0.001 | mA
00317 | [R] | AnalogOutput |  |  |  | 0.001 | mA
00318.0 | [R] | DigitalInputs.DI1 |  |  |  |  | bool
00318.1 | [R] | DigitalInputs.DI2 |  |  |  |  | bool
00318.2 | [R] | DigitalInputs.DI3 |  |  |  |  | bool
00319.0 | [R] | OutputRelays.Relay1 |  |  |  |  | bool
00319.1 | [R] | OutputRelays.Relay2 |  |  |  |  | bool
00319.2 | [R] | OutputRelays.AutoDeareating |  |  |  |  | bool
00320 | [R] | NoOfPowerOns |  |  |  |  | unscaled
00321 | [R] | RunTimeHI |  | Counts the time the DDA pump has been dosing |  | 1 | min
00322 | [R] | RunTimeLO
00323 | [R] | OperatingHoursHI |  | Counts the number of hours the DDA pump has been switched on. |  | 1 | min
00324 | [R] | OperatingHoursLO
00325 | [R] | StrokeCounterHI |  |  |  |  | unscaled
00326 | [R] | StrokeCounterLO
00327 | [R] | TimeToNextDosingHI |  |  |  | 1 | s
00328 | [R] | TimeToNextDosingLO
SIMULATION [R/W]
00701 | [W] | Simulation.AlarmCode |  | Alarm code for alarm simulation (must be different from '0') |  |  | enum
00702 | [W] | Simulation.WarningCode |  |  |  |  | enum
00708 | [W] | Simulation.Activate |  | Switching alarm simulation on and off |  |  | bool
00709 | [R] | Simulation.Active |  | Status of alarm simulation |  |  | bool
USER REGISTERS [R/W]
00751 | [R/W] | UserLabel1 | Saved in EEPROM |  |  |  | unscaled
00752 | [R/W] | UserLabel2 | Saved in EEPROM |  |  |  | unscaled
00753 | [R/W] | UserLabel3 | Saved in EEPROM |  |  |  | unscaled
00754-00799 | [R/W] | UserLabel4...UserLabel49 | Saved in EEPROM |  |  |  | unscaled
00800 | [R/W] | UserLabel50 | Saved in EEPROM |  |  |  | unscaled

## iGRID Receiver
GRUNDFOS iGRID Integration with SCADA systems - iGRID RECEIVER
All addresses are registers (16 bit), and the address is written in decimal format.
Sheet version: V01.00.00
Change date (d-m-y): 27-05-2021
The iGRID Controller is a Modbus Server, All registers are Holding registers.
IP must be static and can be configured to a custom static IP for LAN1, or to a static IP in the DHCP server using LAN2
REG# logic. 4 ciffers. 1st ciffer = box product, xx starting from 01 = product number, 4th ciffer = datapoint
Reg. addr. | Access | Modbus parameter name | Modbus notes - development | Description | Bool/Enum description | Modbus Scale | Modbus Unit
PIT MEASUREMENT POINT [R]
01xx0 | [R] | Supply Temperature | ts |  |  | 0.1 | °C
01xx1 | [R] | Return Temperature | tr |  |  | 0.1 | °C
01xx2 | [R] | Supply Pressure | ps |  |  | 0.01 | bar
01xx3 | [R] | Return Pressure | pr |  |  | 0.01 | bar
01xx4 | [R] | UCAP Voltage | ucap | Supercap used for energy storage voltage |  | 0.001 | V
01xx5 | [R] | GSM Signal | dbm | Signal strength |  | 1 | dbm
01xx6 | [R] | Watchdog | wd | Counts up to 65535, then resets. |  | 1 | Tick
BUILDING MEASUREMENT POINT [R]
02xx0 | [R] | Supply Temperature | ts |  |  | 0.1 | °C
02xx1 | [R] | Return Temperature | tr |  |  | 0.1 | °C
02xx2 | [R] | Supply Pressure | ps |  |  | 0.01 | bar
02xx3 | [R] | Return Pressure | pr |  |  | 0.01 | bar
02xx4 | [R] | UCAP Voltage | ucap | Supercap used for energy storage voltage |  | 0.001 | V
02xx5 | [R] | GSM Signal | dbm | Signal strength |  | 1 | dbm
02xx6 | [R] | Watchdog | wd | Counts up to 65535, then resets. |  | 1 | Tick
MEASUR BUILDING BYPASS [R]
03xx0 | [R] | Supply Temperature | ts |  |  | 0.1 | °C
03xx1 | [R] | Return Temperature | tr |  |  | 0.1 | °C
03xx2 | [R] | Supply Pressure | ps |  |  | 0.01 | bar
03xx3 | [R] | Return Pressure | pr |  |  | 0.01 | bar
03xx4 | [R] | UCAP Voltage | ucap | Supercap used for energy storage voltage |  | 0.001 | V
03xx5 | [R] | GSM Signal | dbm | Signal strength |  | 1 | dbm
03xx6 | [R] | Watchdog | wd | Counts up to 65535, then resets. |  | 1 | Tick
03xx7 | [R] | Valve open | valve_is_open |  | 0 = Closed 1 = Open |  | bool
03xx8 | [R] | Temperature setpoint | tsp |  |  | 0.1 | °C
BYPASS CABINET [R]
04xx0 | [R] | Supply Temperature | ts |  |  | 0.1 | °C
04xx1 | [R] | Return Temperature | tr |  |  | 0.1 | °C
04xx2 | [R] | Supply Pressure | ps |  |  | 0.01 | bar
04xx3 | [R] | Return Pressure | pr |  |  | 0.01 | bar
04xx4 | [R] | UCAP Voltage | ucap | Supercap used for energy storage voltage |  | 0.001 | V
04xx5 | [R] | GSM Signal | dbm | Signal strength |  | 1 | dbm
04xx6 | [R] | Watchdog | wd | Counts up to 65535, then resets. |  | 1 | Tick
04xx7 | [R] | Valve open | valve_is_open |  | 0 = Closed 1 = Open |  | bool
T-ZONE, P-ZONE [R/W]
0(5/6)x00 | [R] | Supply Temperature 1 | ts1 |  |  | 0.1 | °C
0(5/6)x01 | [R] | Supply Temperature 2 | ts2 |  |  | 0.1 | °C
0(5/6)x02 | [R] | Supply Temperature 3 | ts3 |  |  | 0.1 | °C
0(5/6)x03 | [R] | Return Temperature 1 | tr1 |  |  | 0.1 | °C
0(5/6)x04 | [R] | Return Temperature 2 | tr2 |  |  | 0.1 | °C
0(5/6)x05 | [R] | Return Temperature 3 | tr3 |  |  | 0.1 | °C
0(5/6)x06 | [R] | Supply Pressure 1 | ps1 |  |  | 0.01 | bar
0(5/6)x07 | [R] | Supply Pressure 2 | ps2 |  |  | 0.01 | bar
0(5/6)x08 | [R] | Supply Pressure 3 | ps3 |  |  | 0.01 | bar
0(5/6)x09 | [R] | Return Pressure 1 | pr1 |  |  | 0.01 | bar
0(5/6)x10 | [R] | Return Pressure 2 | pr2 |  |  | 0.01 | bar
0(5/6)x11 | [R] | Return Pressure 3 | pr3 |  |  | 0.01 | bar
0(5/6)x12 | [R] | Supply Flow | fls | Used if no shunt |  | 0.1 | m3/h
0(5/6)x13 | [R] | Retrurn Flow | flr |  |  | 0.1 | m3/h
0(5/6)x15 | [R] | Differential Pressure from Main | dp1 |  |  | 0.01 | bar
0(5/6)x16 | [R] | Differential Pressure to Zone | dp2 |  |  | 0.01 | bar
0(5/6)x17 | [R] | Supply Temperature to Zone Setpoint | ts2sp |  |  | 0.1 | °C
0(5/6)x18 | [R] | Supply Pressure to Zone Setpoint | ps2sp |  |  | 0.01 | bar
0(5/6)x19 | [R] | Main Return Pressure Setpoint | pr2sp |  |  | 0.01 | bar
0(5/6)x20 | [R] | Differential Pressure to Zone Setpoint | dp2sp |  |  | 0.01 | bar
0(5/6)x21 | [R] | Indoor Temperature | tin |  |  | 0.1 | °C
0(5/6)x22 | [R] | Pit Water Level Alarm | pwla |  | 0 = No 1 = Yes |  | bool
0(5/6)x30 | [R] | Booster 1 Pump Power | bs1p/br1p |  |  | 1 | W
0(5/6)x31 | [R] | Booster 1 Pump Pct | bs1p/br1p |  |  | 1 | %
0(5/6)x32 | [R] | Booster 1 Pump RPM | bs1spd/br1spd |  |  | 1 | RPM
0(5/6)x33 | [R] | Booster 1 Pump Alarm Code | bs1al/br1al |  |  | 1 | enum
0(5/6)x34 | [R] | Booster 1 Pump Warning Code | bs1wa/br1wa |  |  | 1 | enum
0(5/6)x35 | [R] | Booster 1 Pump Starts Counter High | bs1st/br1st | Same tag, as it is 32bit internally. |  | 1 | Tick
0(5/6)x36 | [R] | Booster 1 Pump Starts Counter Low | bs1st/br1st | Same tag, as it is 32bit internally. |  | 1 | Tick
0(5/6)x37 | [R] | Booster 1 Pump Operation Hours Counter High | bs1hr/br1hr | Same tag, as it is 32bit internally. |  | 1 | hour
0(5/6)x38 | [R] | Booster 1 Pump Operation Hours Counter Low | bs1hr/br1hr | Same tag, as it is 32bit internally. |  | 1 | hour
0(5/6)x39 | [R] | Booster 1 Pump kWh Counter High | bs1e/br1e | Same tag, as it is 32bit internally. |  | 1 | kwh
0(5/6)x40 | [R] | Booster 1 Pump kWh Counter Low | bs1e/br1e | Same tag, as it is 32bit internally. |  | 1 | kwh
0(5/6)x41 | [R] | Booster 1 Pump Blocked | bs1extstp/br1extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
0(5/6)x45 | [R] | Booster 2 Pump Power | bs2p/br2p |  |  | 1 | W
0(5/6)x46 | [R] | Booster 2 Pump Pct | bs2spdpct/br2spdpct |  |  | 1 | %
0(5/6)x47 | [R] | Booster 2 Pump RPM | bs2spd/br2spd |  |  | 1 | RPM
0(5/6)x48 | [R] | Booster 2 Pump Alarm Code | bs2al/br2al |  |  | 1 | enum
0(5/6)x49 | [R] | Booster 2 Pump Warning Code | bs2wa/br2wa |  |  | 1 | enum
0(5/6)x50 | [R] | Booster 2 Pump Starts Counter High | bs2st/br2st | Same tag, as it is 32bit internally. |  | 1 | Tick
0(5/6)x51 | [R] | Booster 2 Pump Starts Counter Low | bs2st/br2st | Same tag, as it is 32bit internally. |  | 1 | Tick
0(5/6)x52 | [R] | Booster 2 Pump Operation Hours Counter High | bs2hr/br2hr | Same tag, as it is 32bit internally. |  | 1 | hour
0(5/6)x53 | [R] | Booster 2 Pump Operation Hours Counter Low | bs2hr/br2hr | Same tag, as it is 32bit internally. |  | 1 | hour
0(5/6)x54 | [R] | Booster 2 Pump kWh Counter High | bs2e/br2e | Same tag, as it is 32bit internally. |  | 1 | kwh
0(5/6)x55 | [R] | Booster 2 Pump kWh Counter Low | bs2e/br2e | Same tag, as it is 32bit internally. |  | 1 | kwh
0(5/6)x56 | [R] | Booster 2 Pump Blocked | bs2extstp/br2extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
0(5/6)x60 | [R] | Shunt 1 Pump Power | sh1p |  |  | 1 | W
0(5/6)x61 | [R] | Shunt 1 Pump Pct | sh1spdpct |  |  | 1 | %
0(5/6)x62 | [R] | Shunt 1 Pump RPM | sh1spd |  |  | 1 | RPM
0(5/6)x63 | [R] | Shunt 1 Pump Alarm Code | sh1al |  |  | 1 | enum
0(5/6)x64 | [R] | Shunt 1 Pump Warning Code | sh1wa |  |  | 1 | enum
0(5/6)x65 | [R] | Shunt 1 Pump Starts Counter High | sh1st | Same tag, as it is 32bit internally. |  | 1 | Tick
0(5/6)x66 | [R] | Shunt 1 Pump Starts Counter Low | sh1st | Same tag, as it is 32bit internally. |  | 1 | Tick
0(5/6)x67 | [R] | Shunt 1 Pump Operation Hours Counter High | sh1hr | Same tag, as it is 32bit internally. |  | 1 | hour
0(5/6)x68 | [R] | Shunt 1 Pump Operation Hours Counter Low | sh1hr | Same tag, as it is 32bit internally. |  | 1 | hour
0(5/6)x69 | [R] | Shunt 1 Pump kWh Counter High | sh1e | Same tag, as it is 32bit internally. |  | 1 | kwH
0(5/6)x70 | [R] | Shunt 1 Pump kWh Counter Low | sh1e | Same tag, as it is 32bit internally. |  | 1 | kwH
0(5/6)x71 | [R] | Shunt 1 Pump Blocked | sh1extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
0(5/6)x75 | [R] | Shunt 2 Pump Power | sh2p |  |  | 1 | W
0(5/6)x76 | [R] | Shunt 2 Pump Pct | sh2spdpct |  |  | 1 | %
0(5/6)x77 | [R] | Shunt 2 Pump RPM | sh2spd |  |  | 1 | RPM
0(5/6)x78 | [R] | Shunt 2 Pump Alarm Code | sh2al |  |  | 1 | enum
0(5/6)x79 | [R] | Shunt 2 Pump Warning Code | sh2wa |  |  | 1 | enum
0(5/6)x80 | [R] | Shunt 2 Pump Starts Counter High | sh1st | Same tag, as it is 32bit internally. |  | 1 | Tick
0(5/6)x81 | [R] | Shunt 2 Pump Starts Counter Low | sh1st | Same tag, as it is 32bit internally. |  | 1 | Tick
0(5/6)x82 | [R] | Shunt 2 Pump Operation Hours Counter High | sh2hr | Same tag, as it is 32bit internally. |  | 1 | hour
0(5/6)x83 | [R] | Shunt 2 Pump Operation Hours Counter Low | sh2hr | Same tag, as it is 32bit internally. |  | 1 | hour
0(5/6)x84 | [R] | Shunt 2 Pump kWh Counter High | sh2e | Same tag, as it is 32bit internally. |  | 1 | kwh
0(5/6)x85 | [R] | Shunt 2 Pump kWh Counter Low | sh2e | Same tag, as it is 32bit internally. |  | 1 | kwh
0(5/6)x86 | [R] | Shunt 2 Pump Blocked | sh2extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
0(5/6)x90 | [R] | Setpoints
0(5/6)x91 | [W] | Setpoints
0(5/6)x92 | [W] | Setpoints
0(5/6)x93 | [W] | Setpoints
0(5/6)x94 | [W] | Setpoints
0(5/6)x95 | [W] | Setpoints
0(5/6)x96 | [W] | Setpoints
0(5/6)x97 | [W] | Setpoints
0(5/6)x98 | [R] | GSM Signal | dbm | Signal strength |  | 1 | dbm
0(5/6)x99 | [R] | Watchdog | wd | Counts up to 65535, then resets. |  | 1 | Tick
SIMULATION [R/W]
07x00 | [R] | Datalogger online PUMP/ZONE | datalogger_online_NAME |  | 0 =PUMP 1 = ZONE |  | bool
07x01 | [R] | Differential pressure setpoint | bs/br_auto_psp |  |  | 0.01 | bar
07x02 | [R] | Grid differential pressure measurepoint 1 | grid_differential_pressure_1_NAME |  |  | 0.01 | bar
07x03 | [R] | Grid data offline counter measurepoint 1 | grid_data_offline_counter_1_NAME |  |  | 1 | Tick
07x04 | [R] | Grid differential pressure measurepoint 2 | grid_differential_pressure_2_NAME |  |  | 0.01 | bar
07x05 | [R] | Grid data offline counter measurepoint 2 | grid_data_offline_counter_2_NAME |  |  | 1 | Tick
07x50 | [W] | PUMP/ZONE supply pressure before pump | ADDRESS/NAME_ps1 |  |  | 0.01 | bar
07x51 | [W] | PUMP/ZONE supply pressure after pump | ADDRESS/NAME_ps2 |  |  | 0.01 | bar
07x52 | [W] | PUMP/ZONE return pressure | ADDRESS/NAME_pr |  |  | 0.01 | bar
07x53 | [W] | PUMP/ZONE supply pressure before pump | ADDRESS/NAME_ps1 |  |  | 0.01 | bar
07x54 | [W] | PUMP/ZONE supply pressure after pump | ADDRESS/NAME_ps2 |  |  | 0.01 | bar
07x55 | [W] | PUMP/ZONE return pressure | ADDRESS/NAME_pr |  |  | 0.01 | bar
07x56 | [W] | PUMP/ZONE supply pressure before pump | ADDRESS/NAME_ps1 |  |  | 0.01 | bar
07x57 | [W] | PUMP/ZONE supply pressure after pump | ADDRESS/NAME_ps2 |  |  | 0.01 | bar
07x58 | [W] | PUMP/ZONE return pressure | ADDRESS/NAME_pr |  |  | 0.01 | bar
07x60 | [W] | Measurepoint 1 supply pressure | ADDRESSmp_ps |  |  | 0.01 | bar
07x61 | [W] | Measurepoint 1 return pressure | ADDRESSmp_pr |  |  | 0.01 | bar
07x62 | [W] | Measurepoint 2 supply pressure | ADDRESSmp_ps |  |  | 0.01 | bar
07x63 | [W] | Measurepoint 2 return pressure | ADDRESSmp_pr |  |  | 0.01 | bar
07x64 | [W] | Measurepoint 3 supply pressure | ADDRESSmp_ps |  |  | 0.01 | bar
07x65 | [W] | Measurepoint 3 return pressure | ADDRESSmp_pr |  |  | 0.01 | bar
07x66 | [W] | Measurepoint 4 supply pressure | ADDRESSmp_ps |  |  | 0.01 | bar
07x67 | [W] | Measurepoint 4 return pressure | ADDRESSmp_pr |  |  | 0.01 | bar
07x68 | [W] | Measurepoint 5 supply pressure | ADDRESSmp_ps |  |  | 0.01 | bar
07x69 | [W] | Measurepoint 5 return pressure | ADDRESSmp_pr |  |  | 0.01 | bar

## iGRID T-Zone & P-Zone
GRUNDFOS iGRID Integration with SCADA systems - iGRID T-ZONE, P-ZONE
All addresses are registers (16 bit), and the address is written in decimal format.
Sheet version: V01.00.00
Change date (d-m-y): 27-05-2021
The iGRID Controller is a Modbus Server, All registers are Holding registers.
IP must be static and can be configured to a custom static IP for LAN1, or to a static IP in the DHCP server using LAN2
Reg. addr. | Access | Modbus parameter name | Modbus notes - development | Description | Bool/Enum description | Modbus Scale | Modbus Unit
SYSTEM DATA [R]
00000 | [R] | Supply Temperature | ts | Used if only one supply Temperature |  | 0.1 | °C
00001 | [R] | Supply Temperature from Main | ts1 | Used if multiple supply Temperature |  | 0.1 | °C
00002 | [R] | Supply Temperature to Zone | ts2 | Used if multiple supply Temperature |  | 0.1 | °C
00003 | [R] | Return Temperature | tr |  |  | 0.1 | °C
00004 | [R] | Supply Pressure | ps | Used if only one supply Pressure |  | 0.01 | bar
00005 | [R] | Supply Pressure from Main | ps1 | Used if multiple supply Pressures |  | 0.01 | bar
00006 | [R] | Supply Pressure to Zone | ps2 | Used if multiple supply Pressures |  | 0.01 | bar
00007 | [R] | Supply Pressure after Reduction | ps3 | Used if third supply Pressure |  | 0.01 | bar
00008 | [R] | Return Pressure | pr | Used if only one return Pressure |  | 0.01 | bar
00009 | [R] | Return Pressure to Main | pr1 | Used if multiple return Pressures |  | 0.01 | bar
00010 | [R] | Return Pressure from Zone | pr2 | Used if multiple return Pressures |  | 0.01 | bar
00011 | [R] | Return Pressure after Strainer | pr3 | Used if third return Pressure |  | 0.01 | bar
00012 | [R] | Supply Flow | fls | Used if no shunt |  | 0.1 | m3/h
00013 | [R] | Supply Flow from Main | fls1 | Used with shunt |  | 0.1 | m3/h
00014 | [R] | Supply Flow to Zone | fls2 | Used with shunt |  | 0.1 | m3/h
00015 | [R] | Return Flow | flr | Used if no shunt |  | 0.1 | m3/h
00016 | [R] | Return Flow to Main | flr1 | Used with shunt |  | 0.1 | m3/h
00017 | [R] | Return Flow from Zone | flr2 | Used with shunt |  | 0.1 | m3/h
00018 | [R] | Indoor Temperature | tin |  |  | 0.1 | °C
00019 | [R] | Outdoor Temperature | to |  |  | 0.1 | °C
00020 | [R] | Pit Water Level Alarm | pwla |  | 0 = No 1 = Yes |  | bool
00021 | [R] | Differential Pressure from Main | dp1 |  |  | 0.01 | bar
00022 | [R] | Differential Pressure to Zone | dp2 |  |  | 0.01 | bar
00023 | [R] | Supply Temperature to Zone Setpoint | ts2sp |  |  | 0.1 | °C
00024 | [R] | Supply Pressure to Zone Setpoint | ps2sp |  |  | 0.01 | bar
00025 | [R] | Main Return Pressure Setpoint | pr2sp |  |  | 0.01 | bar
00026 | [R] | Differential Pressure to Zone Setpoint | dp2sp |  |  | 0.01 | bar
00027 | [R] | Watchdog | wd |  |  | 1 | sec
SENSOR STATUS [R]
00040 | [R] | Supply Temperature Sensor Status | tsst | Used if only one supply Temperature | 0 = No alarm 1 = Alarm |  | enum
00041 | [R] | Supply Temperature from Main Sensor Status | ts1st | Used if multiple supply Temperature | 0 = No alarm 1 = Alarm |  | enum
00042 | [R] | Supply Temperature to Zone Sensor Status | ts2st | Used if multiple supply Temperature | 0 = No alarm 1 = Alarm |  | enum
00043 | [R] | Return Temperature Sensor Status | trst |  | 0 = No alarm 1 = Alarm |  | enum
00044 | [R] | Supply Pressure Sensor Status | psst | Used if only one supply Pressure | 0 = No alarm 1 = Alarm |  | enum
00045 | [R] | Supply Pressure from Main Sensor Status | ps1st | Used if multiple supply Pressures | 0 = No alarm 1 = Alarm |  | enum
00046 | [R] | Supply Pressure to Zone Sensor Status | ps2st | Used if multiple supply Pressures | 0 = No alarm 1 = Alarm |  | enum
00047 | [R] | Supply Pressure after Reduction Sensor Status | ps3st | Used if third supply Pressure | 0 = No alarm 1 = Alarm |  | enum
00048 | [R] | Return Pressure Sensor Status | prst | Used if only one return Pressure | 0 = No alarm 1 = Alarm |  | enum
00049 | [R] | Return Pressure to Main Sensor Status | pr1st | Used if multiple return Pressures | 0 = No alarm 1 = Alarm |  | enum
00050 | [R] | Return Pressure from Zone Sensor Status | pr2st | Used if multiple return Pressures | 0 = No alarm 1 = Alarm |  | enum
00051 | [R] | Return Pressure after Strainer Sensor Status | pr3st | Used if third return Pressure | 0 = No alarm 1 = Alarm |  | enum
00052 | [R] | Supply Flow Meter Status | flsst | Used if no shunt | 0 = No alarm 1 = Alarm |  | enum
00053 | [R] | Supply Flow from Main Meter Status | fls1st | Used with shunt | 0 = No alarm 1 = Alarm |  | enum
00054 | [R] | Supply Flow to Zone Meter Status | fls2st | Used with shunt | 0 = No alarm 1 = Alarm |  | enum
00055 | [R] | Return Flow Meter Status | flrst | Used if no shunt | 0 = No alarm 1 = Alarm |  | enum
00056 | [R] | Return Flow to Main Meter Status | flr1st | Used with shunt | 0 = No alarm 1 = Alarm |  | enum
00057 | [R] | Return Flow from Zone Meter Status | flr2st | Used with shunt | 0 = No alarm 1 = Alarm |  | enum
00058 | [R] | Indoor Temperature Sensor Status | tinst |  | 0 = No alarm 1 = Alarm |  | enum
00059 | [R] | Outdoor Temperature Sensor Status | tost |  | 0 = No alarm 1 = Alarm |  | enum
00060 | [R] | Pit Water Level Alarm Sensor Status | pwlast |  | 0 = No alarm 1 = Alarm |  | enum
SHUNT PUMP [R]
00070 | [R] | Shunt Pump Power | shp |  |  | 1 | W
00071 | [R] | Shunt Pump RPM | shspd |  |  | 1 | RPM
00072 | [R] | Shunt Pump PCT | shspdpct |  |  | 1 | %
00073 | [R] | Shunt Pump Alarm Code | shal | Grundfos-specific alarm code |  |  | enum
00074 | [R] | Shunt Pump Warning Code | shwa | Grundfos-specific warning code |  |  | enum
00075 | [R] | Shunt Pump Starts Counter High | shst | Same tag, as it is 32bit internally. |  | 1 | Tick
00076 | [R] | Shunt Pump Starts Counter Low | shst | Same tag, as it is 32bit internally. |  | 1 | Tick
00077 | [R] | Shunt Pump Operation Hours Counter High | shhr | Same tag, as it is 32bit internally. |  | 1 | hour
00078 | [R] | Shunt Pump Operation Hours Counter Low | shhr | Same tag, as it is 32bit internally. |  | 1 | hour
00079 | [R] | Shunt Pump kWh Counter High | she | Same tag, as it is 32bit internally. |  | 1 | kwh
00080 | [R] | Shunt Pump kWh Counter Low | she | Same tag, as it is 32bit internally. |  | 1 | kwh
00081 | [R] | Shunt Enabled | shen |  | 0 = Disabled 1 = Enabled |  | bool
SHUNT PUMP 1 [R]
00090 | [R] | Shunt Pump 1 Power | sh1p |  |  | 1 | W
00091 | [R] | Shunt Pump 1 RPM | sh1spd |  |  | 1 | RPM
00092 | [R] | Shunt Pump 1 PCT | sh1spdpct |  |  | 1 | %
00093 | [R] | Shunt Pump 1 Alarm Code | sh1al | Grundfos-specific alarm code |  |  | enum
00094 | [R] | Shunt Pump 1 Warning Code | sh1wa | Grundfos-specific warning code |  |  | enum
00095 | [R] | Shunt Pump 1 Starts Counter High | sh1st | Same tag, as it is 32bit internally. |  | 1 | Tick
00096 | [R] | Shunt Pump 1 Starts Counter Low | sh1st | Same tag, as it is 32bit internally. |  | 1 | Tick
00097 | [R] | Shunt Pump 1 Operation Hours Counter High | sh1hr | Same tag, as it is 32bit internally. |  | 1 | hour
00098 | [R] | Shunt Pump 1 Operation Hours Counter Low | sh1hr | Same tag, as it is 32bit internally. |  | 1 | hour
00099 | [R] | Shunt Pump 1 kWh Counter High | sh1e | Same tag, as it is 32bit internally. |  | 1 | kwh
00100 | [R] | Shunt Pump 1 kWh Counter Low | sh1e | Same tag, as it is 32bit internally. |  | 1 | kwh
00101 | [R] | Shunt Pump 1 Blocked | sh1extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
SHUNT PUMP 2 [R]
00110 | [R] | Shunt Pump 2 Power | sh2p |  |  | 1 | W
00111 | [R] | Shunt Pump 2 RPM | sh2spd |  |  | 1 | RPM
00112 | [R] | Shunt Pump 2 PCT | sh2spdpct |  |  | 1 | %
00113 | [R] | Shunt Pump 2 Alarm Code | sh2al | Grundfos-specific alarm code |  |  | enum
00114 | [R] | Shunt Pump 2 Warning Code | sh2wa | Grundfos-specific warning code |  |  | enum
00115 | [R] | Shunt Pump 2 Starts Counter High | sh2st | Same tag, as it is 32bit internally. |  | 1 | Tick
00116 | [R] | Shunt Pump 2 Starts Counter Low | sh2st | Same tag, as it is 32bit internally. |  | 1 | Tick
00117 | [R] | Shunt Pump 2 Operation Hours Counter High | sh2hr | Same tag, as it is 32bit internally. |  | 1 | hour
00118 | [R] | Shunt Pump 2 Operation Hours Counter Low | sh2hr | Same tag, as it is 32bit internally. |  | 1 | hour
00119 | [R] | Shunt Pump 2 kWh Counter High | sh2e | Same tag, as it is 32bit internally. |  | 1 | kwh
00120 | [R] | Shunt Pump 2 kWh Counter Low | sh2e | Same tag, as it is 32bit internally. |  | 1 | kwh
00121 | [R] | Shunt Pump 2 Blocked | sh2extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
BOOSTER PUMP SUPPLY [R]
00130 | [R] | Booster Pump Supply Power | bsp |  |  | 1 | W
00131 | [R] | Booster Pump Supply RPM | bsspd |  |  | 1 | RPM
00132 | [R] | Booster Pump Supply PCT | bsspdpct |  |  | 1 | %
00133 | [R] | Booster Pump Supply Alarm Code | bsal | Grundfos-specific alarm code |  |  | enum
00134 | [R] | Booster Pump Supply Warning Code | bswa | Grundfos-specific warning code |  |  | enum
00135 | [R] | Booster Pump Supply Starts Counter High | bsst | Same tag, as it is 32bit internally. |  | 1 | Tick
00136 | [R] | Booster Pump Supply Starts Counter Low | bsst | Same tag, as it is 32bit internally. |  | 1 | Tick
00137 | [R] | Booster Pump Supply Operation Hours Counter High | bshr | Same tag, as it is 32bit internally. |  | 1 | hour
00138 | [R] | Booster Pump Supply Operation Hours Counter Low | bshr | Same tag, as it is 32bit internally. |  | 1 | hour
00139 | [R] | Booster Pump Supply kWh Counter High | bse | Same tag, as it is 32bit internally. |  | 1 | kwh
00140 | [R] | Booster Pump Supply kWh Counter Low | bse | Same tag, as it is 32bit internally. |  | 1 | kwh
00141 | [R] | Booster Supply Enabled | bsen |  | 0 = Disabled 1 = Enabled |  | bool
BOOSTER PUMP SUPPLY 1 [R]
00150 | [R] | Booster Pump Supply 1 Power | bs1p |  |  | 1 | W
00151 | [R] | Booster Pump Supply 1 RPM | bs1spd |  |  | 1 | RPM
00152 | [R] | Booster Pump Supply 1 PCT | bs1spdpct |  |  | 1 | %
00153 | [R] | Booster Pump Supply 1 Alarm Code | bs1al | Grundfos-specific alarm code |  |  | enum
00154 | [R] | Booster Pump Supply 1 Warning Code | bs1wa | Grundfos-specific warning code |  |  | enum
00155 | [R] | Booster Pump Supply 1 Starts Counter High | bs1st | Same tag, as it is 32bit internally. |  | 1 | Tick
00156 | [R] | Booster Pump Supply 1 Starts Counter Low | bs1st | Same tag, as it is 32bit internally. |  | 1 | Tick
00157 | [R] | Booster Pump Supply 1 Operation Hours Counter High | bs1hr | Same tag, as it is 32bit internally. |  | 1 | hour
00158 | [R] | Booster Pump Supply 1 Operation Hours Counter Low | bs1hr | Same tag, as it is 32bit internally. |  | 1 | hour
00159 | [R] | Booster Pump Supply 1 kWh Counter High | bs1e | Same tag, as it is 32bit internally. |  | 1 | kwh
00160 | [R] | Booster Pump Supply 1 kWh Counter Low | bs1e | Same tag, as it is 32bit internally. |  | 1 | kwh
00161 | [R] | Booster Pump Supply 1 Blocked | bs1extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
BOOSTER PUMP SUPPLY 2 [R]
00170 | [R] | Booster Pump Supply 2 Power | bs2p |  |  | 1 | W
00171 | [R] | Booster Pump Supply 2 RPM | bs2spd |  |  | 1 | RPM
00172 | [R] | Booster Pump Supply 2 PCT | bs2spdpct |  |  | 1 | %
00173 | [R] | Booster Pump Supply 2 Alarm Code | bs2al | Grundfos-specific alarm code |  |  | enum
00174 | [R] | Booster Pump Supply 2 Warning Code | bs2wa | Grundfos-specific warning code |  |  | enum
00175 | [R] | Booster Pump Supply 2 Starts Counter High | bs2st | Same tag, as it is 32bit internally. |  | 1 | Tick
00176 | [R] | Booster Pump Supply 2 Starts Counter Low | bs2st | Same tag, as it is 32bit internally. |  | 1 | Tick
00177 | [R] | Booster Pump Supply 2 Operation Hours Counter High | bs2hr | Same tag, as it is 32bit internally. |  | 1 | hour
00178 | [R] | Booster Pump Supply 2 Operation Hours Counter Low | bs2hr | Same tag, as it is 32bit internally. |  | 1 | hour
00179 | [R] | Booster Pump Supply 2 kWh Counter High | bs2e | Same tag, as it is 32bit internally. |  | 1 | kwh
00180 | [R] | Booster Pump Supply 2 kWh Counter Low | bs2e | Same tag, as it is 32bit internally. |  | 1 | kwh
00181 | [R] | Booster Pump Supply 2 Blocked | bs2extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
BOOSTER PUMP RETURN [R]
00190 | [R] | Booster Pump Return Power | brp |  |  | 1 | W
00191 | [R] | Booster Pump Return RPM | brspd |  |  | 1 | RPM
00192 | [R] | Booster Pump Return PCT | brspdpct |  |  | 1 | %
00193 | [R] | Booster Pump Return Alarm Code | bral | Grundfos-specific alarm code |  |  | enum
00194 | [R] | Booster Pump Return Warning Code | brwa | Grundfos-specific warning code |  |  | enum
00195 | [R] | Booster Pump Return Starts Counter High | brst | Same tag, as it is 32bit internally. |  | 1 | Tick
00196 | [R] | Booster Pump Return Starts Counter Low | brst | Same tag, as it is 32bit internally. |  | 1 | Tick
00197 | [R] | Booster Pump Return Operation Hours Counter High | brhr | Same tag, as it is 32bit internally. |  | 1 | hour
00198 | [R] | Booster Pump Return Operation Hours Counter Low | brhr | Same tag, as it is 32bit internally. |  | 1 | hour
00199 | [R] | Booster Pump kWh Counter High | bre | Same tag, as it is 32bit internally. |  | 1 | kwh
00200 | [R] | Booster Pump kWh Counter Low | bre | Same tag, as it is 32bit internally. |  | 1 | kwh
00201 | [R] | Booster Return Enabled | bren |  | 0 = Disabled 1 = Enabled |  | bool
BOOSTER PUMP RETURN 1 [R]
00210 | [R] | Booster Pump Return 1 Power | br1p |  |  | 1 | W
00211 | [R] | Booster Pump Return 1 RPM | br1spd |  |  | 1 | RPM
00212 | [R] | Booster Pump Return 1 PCT | br1spdpct |  |  | 1 | %
00213 | [R] | Booster Pump Return 1 Alarm Code | br1al | Grundfos-specific alarm code |  | 1 | enum
00214 | [R] | Booster Pump Return 1 Warning Code | br1wa | Grundfos-specific warning code |  | 1 | enum
00215 | [R] | Booster Pump Return 1 Starts Counter High | br1st | Same tag, as it is 32bit internally. |  | 1 | Tick
00216 | [R] | Booster Pump Return 1 Starts Counter Low | br1st | Same tag, as it is 32bit internally. |  | 1 | Tick
00217 | [R] | Booster Pump Return 1 Operation Hours Counter High | br1hr | Same tag, as it is 32bit internally. |  | 1 | hour
00218 | [R] | Booster Pump Return 1 Operation Hours Counter Low | br1hr | Same tag, as it is 32bit internally. |  | 1 | hour
00219 | [R] | Booster Pump Return 1 kWh Counter High | br1e | Same tag, as it is 32bit internally. |  | 1 | kwh
00220 | [R] | Booster Pump Return 1 kWh Counter Low | br1e | Same tag, as it is 32bit internally. |  | 1 | kwh
00221 | [R] | Booster Pump Return 1 Blocked | br1extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
BOOSTER PUMP RETURN 2 [R]
00230 | [R] | Booster Pump Return 2 Power | br2p |  |  | 1 | W
00231 | [R] | Booster Pump Return 2 RPM | br2spd |  |  | 1 | RPM
00232 | [R] | Booster Pump Return 2 PCT | br2spdpct |  |  | 1 | %
00233 | [R] | Booster Pump Return 2 Alarm Code | br2al | Grundfos-specific alarm code |  |  | enum
00234 | [R] | Booster Pump Return 2 Warning Code | br2wa | Grundfos-specific warning code |  |  | enum
00235 | [R] | Booster Pump Return 2 Starts Counter High | br2st | Same tag, as it is 32bit internally. |  | 1 | Tick
00236 | [R] | Booster Pump Return 2 Starts Counter Low | br2st | Same tag, as it is 32bit internally. |  | 1 | Tick
00237 | [R] | Booster Pump Return 2 Operation Hours Counter High | br2hr | Same tag, as it is 32bit internally. |  | 1 | hour
00238 | [R] | Booster Pump Return 2 Operation Hours Counter Low | br2hr | Same tag, as it is 32bit internally. |  | 1 | hour
00239 | [R] | Booster Pump Return 2 kWh Counter High | br2e | Same tag, as it is 32bit internally. |  | 1 | kwh
00240 | [R] | Booster Pump Return 2 kWh Counter Low | br2e | Same tag, as it is 32bit internally. |  | 1 | kwh
00241 | [R] | Booster Pump Return 2 Blocked | br2extstp |  | 0 =Enabled 1 = Forced to stop |  | bool
PRESSURE HOLDING VALVE [R]
00250 | R | Pressure Holding Valve Setpoint | pr2sp |  |  | 0.01 | bar
00251 | R | Pressure Holding Valve Actual Position | phvrpct |  |  | 0.1 | %
PRESSURE REDUCTION VALVE [R]
00260 | R | Pressure Reduction Valve Setpoint | ps2sp |  |  | 0.01 | bar
00261 | R | Pressure Reduction Valve Actual Position | prvrpct |  |  | 0.1 | %
CONTROL [W]
00300 | [W] | Shunt External Control Enabled | sh_ext_Control_Enabled |  | 0 = Disabled 1 = Enabled |  | enum
00301 | [W] | Shunt External Mode | sh_ext_mode |  | 0 = Stop 1 = Manual 2 = Auto |  | enum
00302 | [W] | Shunt External Manual Temperature Setpoint | sh_ext_manual_tsp |  |  | 0.1 | °C
00303 | [W] | Booster Supply External Control Enabled | bs_ext_Control_Enabled |  | 0 = Disabled 1 = Enabled |  | enum
00304 | [W] | Booster Supply External Mode | bs_ext_mode |  | 0 = Stop 1 = Manual 2 = Auto |  | enum
00305 | [W] | Booster Supply External Manual Pressure Setpoint | bs_ext_manual_psp |  |  | 0.01 | bar
00306 | [W] | Booster Return External Control Enabled | br_ext_Control_Enabled |  | 0 = Disabled 1 = Enabled |  | enum
00307 | [W] | Booster Return External Mode | br_ext_mode |  | 0 = Stop 1 = Manual 2 = Auto |  | enum
00308 | [W] | Booster Return External Manual Pressure Setpoint | br_ext_manual_psp |  |  | 0.01 | bar
CUSTOM SENSOR [R]
00400 | [R] | Custom sensor 1
00401 | [R] | Custom sensor 1
00402 | [R] | Custom sensor 1
00403 | [R] | Custom sensor 1
00404 | [R] | Custom sensor 1
00405 | [R] | Custom sensor 1
00406 | [R] | Custom sensor 1
00407 | [R] | Custom sensor 1